## Lines
|  |  | Substation_1 |  | Substation_2 |  |  | Maximum Current Imax (A) | [6 empty] | Dynamic line rating (DLR) |  | Electrical Parameters
NE_name | EIC_Code | TSO | Full_name | Short_name | Full_name | Short_name | Voltage_level(kV) | Period 1 | Period 2 | Period 3 | Period 4 | Period 5 | Period 6 | Fixed | DLRmin(A) | DLRmax(A) | Resistance_R(Ω) | Reactance_X(Ω) | Susceptance_B(μS) | Length_(km) | Comment
Y-Altenkleusheim (-Bixterheide - Opladen) BIGGE O | 11T0-0000-0120-F | Amprion GmbH | Altenkleusheim | D7AKLE2 | Y-Bixterheide | D7YBIX2 | 220 | - | - | - | - | - | - | - | 740 | 1031 | 4.915 | 21.16 | 144.3 | 52.767
Y-Bixterheide (-Altenkleusheim - Opladen) BIGGE O | 11T0-0000-0175-H | Amprion GmbH | Bixterheide | D7BIXT2 | Y-Bixterheide | D7YBIX2 | 220 | - | - | - | - | - | - | - | 1160 | 1392 | 0.665 | 3.721 | 43.6 | 12.1631
Y-Opladen (-Altenkleusheim - Bixterheide) BIGGE O | 11T0-0000-0419-E | Amprion GmbH | Opladen | D7OPLA2 | Y-Bixterheide | D7YBIX2 | 220 | - | - | - | - | - | - | - | 1160 | 1392 | 3.144 | 17.05 | 218.1 | 58.232
Y-Altenkleusheim (-Garenfeld - Opladen) BIGGE W | 11T0-0000-0114-7 | Amprion GmbH | Altenkleusheim | D7AKLE2 | Y-Garenfeld | D7YGAR2 | 220 | - | - | - | - | - | - | - | 740 | 1031 | 4.915 | 21.15 | 144.2 | 52.7362
Y-Garenfeld (-Altenkleusheim - Opladen) BIGGE W | 11T0-0000-0274-F | Amprion GmbH | Garenfeld | D7GARE2 | Y-Garenfeld | D7YGAR2 | 220 | - | - | - | - | - | - | - | 1143 | 1378 | 0.722 | 4.042 | 27.4 | 10.0495
Y-Opladen (-Altenkleusheim - Garenfeld) BIGGE W | 11T0-0000-0420-0 | Amprion GmbH | Opladen | D7OPLA2 | Y-Garenfeld | D7YGAR2 | 220 | - | - | - | - | - | - | - | 1293 | 1392 | 3.144 | 17.05 | 218 | 58.2186
Mittelbexbach - Uchtelfangen BLIES N | 11T0-0000-0740-E | Amprion GmbH | Mittelbexbach | D7MITB1 | Uchtelfangen | D7UCHT1 | 380 | - | - | - | - | - | - | - | 2580 | 3150 | 0.598 | 5.092 | 88.8 | 20.3059 | DLR values under investigation
Mittelbexbach - Uchtelfangen BLIES S | 11T0-0000-0741-B | Amprion GmbH | Mittelbexbach | D7MITB1 | Uchtelfangen | D7UCHT1 | 380 | - | - | - | - | - | - | - | 2580 | 3150 | 0.598 | 5.107 | 88.6 | 20.3129 | DLR values under investigation
Hanekenfaehr - Westerkappeln BRAMGAU | 11T0-0000-0642-D | Amprion GmbH | Hanekenfaehr | D7HANE1 | Westerkappeln | D7WEST1 | 380 | - | - | - | - | - | - | 2565 | - | - | 1.65 | 15.26 | 264.5 | 60.6683
Y-Voehringen (-Buers - Werben) DELLM O | 11T0-0000-1374-4 | Amprion GmbH | Voehringen | D7VOEH2 | Y-Werben | D73YWB2 | 220 | - | - | - | - | - | - | 1220 | - | - | 6.622 | 42.77 | 431.6 | 129.7423
Y-Hoheneck (-Dellmensingen - Voehringen) DONAU O | 11T0-0000-0957-G | Amprion GmbH | Hoheneck | D7HONE1 | Y-Voehringen | D7YVOE1 | 380 | - | - | - | - | - | - | - | 2440 | 3150 | 2.849 | 25.57 | 418.5 | 98.7835 | DLR values under investigation
Y-Voehringen (-Dellmensingen - Hoheneck) DONAU O | 11T0-0000-0956-J | Amprion GmbH | Voehringen | D7VOEH1 | Y-Voehringen | D7YVOE1 | 380 | - | - | - | - | - | - | - | 2580 | 3096 | 0.465 | 4.311 | 74.7 | 17.1364 | DLR values under investigation
Eller - St. Peter ELLER W | 11T0-0000-0495-V | Amprion GmbH | Eller | D7ELLE2 | St. Peter | D7PETE2 | 220 | - | - | - | - | - | - | - | 1104 | 1344 | 0.919 | 5.496 | 51.4 | 16.05 | DLR values under investigation
Diefflen - Ensdorf ENSDF N | 11T0-0000-1672-W | Amprion GmbH | Diefflen | D7DIEF2 | Ensdorf | XEN_SA2 | 220 | - | - | - | - | - | - | 1160 | - | - | 0.66 | 3.7 | 56.9 | 13.8557
Y-Diefflen (-Ensdorf - Uchtelfangen) ENSDF S | 11T0-0000-0218-R | Amprion GmbH | Diefflen | D7DIEF2 | Y-Diefflen | D7YDIE2 | 220 | - | - | - | - | - | - | - | 740 | 1031 | 0.2 | 1.34 | 19.9 | 4.9312 | DLR values under investigation
Y-Ensdorf (-Diefflen - Uchtelfangen) ENSDF S | 11T0-0000-0265-G | Amprion GmbH | Ensdorf | XEN_SA2 | Y-Diefflen | D7YDIE2 | 220 | - | - | - | - | - | - | 1360 | - | - | 0.34 | 1.9 | 40 | 8.3249
Y-Uchtelfangen (-Diefflen - Ensdorf) ENSDF S | 11T0-0000-0511-X | Amprion GmbH | Uchtelfangen | D7UCHT2 | Y-Diefflen | D7YDIE2 | 220 | - | - | - | - | - | - | 1360 | - | - | 0.94 | 5.15 | 108.7 | 22.5938
Buescherhof - Nordlicht ESSEN W | 11T0-0000-0763-Y | Amprion GmbH | Buescherhof | D7BUES1 | Nordlicht | D7NLIC1 | 380 | - | - | - | - | - | - | 2720 | - | - | 0.397 | 3.681 | 63.6 | 14.6111
Gundelfingen - Voehringen GUENZ N | 11T0-0000-0625-C | Amprion GmbH | Gundelfingen | D7GUND1 | Voehringen | D7VOEH1 | 380 | - | - | - | - | - | - | 2720 | - | - | 1.225 | 11.65 | 201.8 | 46.3015
Gundelfingen - Voehringen GUENZ S | 11T0-0000-0626-9 | Amprion GmbH | Gundelfingen | D7GUND1 | Voehringen | D7VOEH1 | 380 | - | - | - | - | - | - | - | 2720 | 3150 | 1.255 | 11.61 | 201.5 | 46.1876
Dauersberg - Limburg LIMBG W | 11T0-0000-1515-F | Amprion GmbH | Dauersberg | D7DAUR1 | Limburg | D7LIMB1 | 380 | - | - | - | - | - | - | 2720 | - | - | 1.264 | 11.86 | 200.1 | 46.5197
Kusenhorst - Niederrhein LIPPE N | 11T0-0000-0680-3 | Amprion GmbH | Kusenhorst | D7KUSE1 | Niederrhein | D7NRHE1 | 380 | - | - | - | - | - | - | - | 2580 | 3096 | 1.026 | 9.514 | 158.9 | 37.1291 | DLR values under investigation
Y-Nordlicht (-Kusenhorst - Niederrhein) LIPPE S | 11T0-0000-1537-1 | Amprion GmbH | Nordlicht | D7NLIC1 | Y-Kusenhorst | D7YKUS1 | 380 | - | - | - | - | - | - | 2720 | - | - | 0.35 | 3.48 | 52.2 | 12.8705
Y-Niederrhein (-Kusenhorst - Nordlicht) LIPPE S | 11T0-0000-1536-4 | Amprion GmbH | Niederrhein | D7NRHE1 | Y-Kusenhorst | D7YKUS1 | 380 | - | - | - | - | - | - | 2720 | - | - | 0.72 | 6.65 | 116.2 | 26.5452
Y-Kusenhorst (-Niederrhein - Nordlicht) LIPPE S | 11T0-0000-1535-7 | Amprion GmbH | Kusenhorst | D7KUSE1 | Y-Kusenhorst | D7YKUS1 | 380 | - | - | - | - | - | - | 2580 | - | - | 0.31 | 2.77 | 46.1 | 10.791
Duennwald - Gremberghoven MERHM O | 11T0-0000-0234-V | Amprion GmbH | Duennwald | D7DUEN2 | Gremberghoven | D7GREM2 | 220 | - | - | - | - | - | - | - | 888 | 1506 | 0.668 | 3.684 | 39.8 | 11.5631
Duennwald - Gremberghoven MERHM W | 11T0-0000-0235-S | Amprion GmbH | Duennwald | D7DUEN2 | Gremberghoven | D7GREM2 | 220 | - | - | - | - | - | - | - | 888 | 1506 | 0.668 | 3.684 | 39.8 | 11.5631
Diefflen - Saarwellingen NALBA O | 11T0-0000-0223-1 | Amprion GmbH | Diefflen | D7DIEF2 | Saarwellingen | D7SAAR2 | 220 | - | - | - | - | - | - | 581 | - | - | 0.057 | 0.331 | 3.7 | 1.0568
Diefflen - Saarwellingen NALBA W | 11T0-0000-0224-Z | Amprion GmbH | Diefflen | D7DIEF2 | Saarwellingen | D7SAAR2 | 220 | - | - | - | - | - | - | 581 | - | - | 0.11 | 0.477 | 3.7 | 1.2686
Sechtem - Weissenthurm NETTE O | 11T0-0000-0477-X | Amprion GmbH | Sechtem | D7SECH2 | Weissenthurm | D7WTHU2 | 220 | - | - | - | - | - | - | - | 1360 | 1632 | 1.686 | 15.66 | 279.7 | 63.1995 | DLR values under investigation
Meckenheim - Weissenthurm NETTE W | 11T0-0000-0717-5 | Amprion GmbH | Meckenheim | D7MECK1 | Weissenthurm | D7WTHU1 | 380 | - | - | - | - | - | - | 2720 | - | - | 1.117 | 10.23 | 182 | 41.2045
St. Peter - Rommerskirchen PETER S | 11T0-0000-0856-O | Amprion GmbH | St. Peter | D7PETE1 | Rommerskirchen | D7ROKI1 | 380 | - | - | - | - | - | - | 2720 | - | - | 0.492 | 4.728 | 76.7 | 18.1848
Y-Hanekenfaehr (-Oechtel - Roxel) ROXEL O | 11T0-0000-0930-8 | Amprion GmbH | Hanekenfaehr | D7HANE1 | Y-Oechtel | D7YOEC1 | 380 | - | - | - | - | - | - | - | 2580 | 3078 | 0.571 | 4.887 | 84.2 | 19.3708
Y-Oechtel (-Hanekenfaehr - Roxel) ROXEL O | 11T0-0000-0931-5 | Amprion GmbH | Oechtel | D7OECH1 | Y-Oechtel | D7YOEC1 | 380 | - | - | - | - | - | - | 820 | - | - | 0.006 | 0.064 | 1.4 | 0.28584
Y-Roxel (-Hanekenfaehr - Oechtel) ROXEL O | 11T0-0000-0932-2 | Amprion GmbH | Roxel | D7ROXE1 | Y-Oechtel | D7YOEC1 | 380 | - | - | - | - | - | - | - | 2580 | 3078 | 1.491 | 12.78 | 222.7 | 50.9445
Y-Oberzier (-Dahlem - Rommersheim) SELHN O | 11T0-0000-0783-Q | Amprion GmbH | Oberzier | D7OBZI1 | Y-Dahlem | D7YDAH1 | 380 | - | - | - | - | - | - | - | 2580 | 2770 | 1.784 | 15.24 | 264.1 | 60.5826
Y-Rommersheim (-Dahlem - Oberzier) SELHN O | 11T0-0000-1629-V | Amprion GmbH | Rommersheim | D7ROMH1 | Y-Dahlem | D7YDAH1 | 380 | - | - | - | - | - | - | - | 2580 | 3096 | 0.71 | 6.09 | 105.4 | 24.1936 | DLR values under investigation
Y-Niederstedem (-Dahlem - Oberzier) SELHN W | 11T0-0000-0762-0 | Amprion GmbH | Niederstedem | D7NSTE1 | Y-Dahlem | D7YDAH1 | 380 | - | - | - | - | - | - | - | 2580 | 2770 | 1.703 | 14.68 | 253.7 | 58.2767 | DLR values under investigation
Y-Oberzier (-Dahlem - Niederstedem) SELHN W | 11T0-0000-0784-N | Amprion GmbH | Oberzier | D7OBZI1 | Y-Dahlem | D7YDAH1 | 380 | - | - | - | - | - | - | - | 2580 | 2770 | 1.784 | 15.24 | 264.2 | 60.5941 | DLR values under investigation
Y-Altenkleusheim (-Eiserfeld - Setzer Wiese) SETZE N | 11T0-0000-1441-K | Amprion GmbH | Altenkleusheim | D7AKLE2 | Y-Setzer Wiese | D7YSET2 | 220 | - | - | - | - | - | - | - | 740 | 888 | 0.687 | 2.938 | 20.1 | 7.3383
Y-Eiserfeld (-Altenkleusheim - Setzer Wiese) SETZE N | 11T0-0000-1442-H | Amprion GmbH | Eiserfeld | D7EISE2 | Y-Setzer Wiese | D7YSET2 | 220 | - | - | - | - | - | - | - | 740 | 888 | 1.436 | 6.377 | 63 | 19.1403
Y-Setzer Wiese (-Altenkleusheim - Eiserfeld) SETZE N | 11T0-0000-1443-E | Amprion GmbH | Setzer Wiese | D7SETZ2 | Y-Setzer Wiese | D7YSET2 | 220 | - | - | - | - | - | - | - | 1360 | 1632 | 0.316 | 1.692 | 22.1 | 5.8394
Y-Brauweiler (-Opladen - Rommerskirchen) STOMM N | 11T0-0000-0416-N | Amprion GmbH | Brauweiler | D7BRAU2 | Y-Rommerskirchen | D7YROK2 | 220 | - | - | - | - | - | - | 1290 | - | - | 0.152 | 2.662 | 53.5 | 11.396
Y-Opladen (-Brauweiler - Rommerskirchen) STOMM N | 11T0-0000-0416-N | Amprion GmbH | Opladen | D7OPLA2 | Y-Rommerskirchen | D7YROK2 | 220 | - | - | - | - | - | - | 1290 | - | - | 1.321 | 7.386 | 83.1 | 23.6579
Y-Rommerskirchen (-Brauweiler - Opladen) STOMM N | 11T0-0000-0416-N | Amprion GmbH | Rommerskirchen | D7ROKI2 | Y-Rommerskirchen | D7YROK2 | 220 | - | - | - | - | - | - | 1290 | - | - | 0.005 | 0.05 | 0.4 | 0.13505
Fuehlingen - Rommerskirchen STOMM S | 11T0-0000-0267-A | Amprion GmbH | Fuehlingen | D7FUEH2 | Rommerskirchen | D7ROKI2 | 220 | - | - | - | - | - | - | - | 1360 | 1632 | 1.024 | 5.516 | 71.8 | 19.004
Rommerskirchen - Sechtem VILLE O | 11T0-0000-0831-A | Amprion GmbH | Rommerskirchen | D7ROKI1 | Sechtem | D7SECH1 | 380 | - | - | - | - | - | - | - | 2580 | 3150 | 1.001 | 8.591 | 148.8 | 34.1425 | DLR values under investigation
Rommerskirchen - Sechtem VILLE W | 11T0-0000-1011-F | Amprion GmbH | Rommerskirchen | D7ROKI1 | Sechtem | D7SECH1 | 380 | - | - | - | - | - | - | - | 2580 | 3096 | 0.989 | 8.594 | 148.9 | 34.1599 | DLR values under investigation
Amelsbueren - Gersteinwerk WERSE W | 11T0-0000-0281-K | Amprion GmbH | Amelsbueren | D7AMEL2 | Gersteinwerk | D7GERS2 | 220 | - | - | - | - | - | - | - | 1290 | 1539 | 1.655 | 8.318 | 104.8 | 28.1943 | DLR values under investigation
Y-Oberottmarshausen (-Bidingen - Leupolz) ALLG O | 11T0-0000-0769-G | Amprion GmbH | Oberottmarshausen | D7OOTT1 | Y-Bidingen | D7BIDI1 | 380 | - | - | - | - | - | - | 2720 | - | - | 1.37 | 12.68 | 220.9 | 50.5393
Y-Altenkleusheim (-Eiserfeld - Setzer Wiese) EISERF | 11T0-0000-0121-C | Amprion GmbH | Altenkleusheim | D7AKLE2 | Y-Setzer Wiese | D7YSET2 | 220 | - | - | - | - | - | - | 740 | - | - | 0.686 | 2.938 | 20.1 | 7.3383
Y-Eiserfeld (-Altenkleusheim - Setzerwiese) EISERF | 11T0-0000-0248-F | Amprion GmbH | Eiserfeld | D7EISE2 | Y-Setzer Wiese | D7YSET2 | 220 | - | - | - | - | - | - | 960 | - | - | 1.148 | 5.413 | 59.2 | 17.0943
Y-Setzer Wiese (-Altenkleusheim - Eiserfeld) EISERF | 11T0-0000-1377-W | Amprion GmbH | Setzer Wiese | D7SETZ2 | Y-Setzer Wiese | D7YSET2 | 220 | - | - | - | - | - | - | 1360 | - | - | 0.315 | 1.688 | 22.1 | 5.8325
Y-Hanekenfaehr (-Kottigerhook - Kusenhorst) MUENST | 11T0-0000-0643-A | Amprion GmbH | Hanekenfaehr | D7HANE1 | Y-Hanekenfaehr | D7YHAN1 | 380 | - | - | - | - | - | - | - | 2580 | 2872 | 1.477 | 13.56 | 203.3 | 50.1383 | DLR values under investigation
Y-Kottigerhook (-Hanekenfaehr - Kusenhorst) MUENST | 11T0-0000-0669-L | Amprion GmbH | Kottigerhook | D7KOTT1 | Y-Hanekenfaehr | D7YHAN1 | 380 | - | - | - | - | - | - | 505 | - | - | 0.005 | 0.05 | 0.4 | 0.13505
Y-Kusenhorst (-Hanekenfaehr - Kottigerhook) MUENST | 11T0-0000-0684-S | Amprion GmbH | Kusenhorst | D7KUSE1 | Y-Hanekenfaehr | D7YHAN1 | 380 | - | - | - | - | - | - | - | 2580 | 2872 | 1.784 | 16.34 | 245.8 | 60.5185 | DLR values under investigation
Y-Pfungstadt (-Bischofsheim - Buerstadt) RIED W | 11T0-0000-0819-V | Amprion GmbH | Pfungstadt | D7PFUN1 | Y-Pfungstadt | D7YPFU1 | 380 | - | - | - | - | - | - | - | 2760 | 3150 | 0.009 | 0.079 | 1.4 | 0.31758 | DLR values under investigation
Y-Buerstadt (-Bischofsheim - Pfungstadt) RIED W | 11T0-0000-0573-3 | Amprion GmbH | Buerstadt | D7BUER1 | Y-Pfungstadt | D7YPFU1 | 380 | - | - | - | - | - | - | - | 2760 | 3150 | 0.796 | 7.832 | 130.1 | 30.4822 | DLR values under investigation
Y-Bischofsheim (-Buerstadt - Pfungstadt) RIED W | 11T0-0000-0563-7 | Amprion GmbH | Bischofsheim | D7BISC1 | Y-Pfungstadt | D7YPFU1 | 380 | - | - | - | - | - | - | - | 2720 | 3150 | 0.666 | 6.539 | 109.1 | 25.5058 | DLR values under investigation
Gronau - Kusenhorst HAMALD | 11T0-0000-0618-7 | Amprion GmbH | Gronau | - | Kusenhorst 1 | D7KUSE1 | 380 | - | - | - | - | - | - | - | 2580 | 3150 | 1.89 | 17.33 | 259.9 | 64.0876 | DLR values under investigation
Meitingen - Oberottmarshausen AUGSBU O | 11T0-0000-0724-A | Amprion GmbH | Meitingen | D7MEIT1 | Oberottmarshausen | D7OOTT1 | 380 | - | - | - | - | - | - | 2720 | - | - | 1.408 | 13.26 | 221.6 | 51.764
Lechhausen - Oberottmarshausen AUGSBU W | 11T0-0000-0694-O | Amprion GmbH | Lechhausen | D7LECH1 | Oberottmarshausen | D7OOTT1 | 380 | - | - | - | - | - | - | 2720 | - | - | 0.961 | 9.01 | 152 | 35.3391
Meckenheim - Sechtem BGEIST W | 11T0-0000-0843-0 | Amprion GmbH | Meckenheim | D7MECK1 | Sechtem | D7SECH1 | 380 | - | - | - | - | - | - | 2720 | - | - | 0.571 | 5.513 | 98.7 | 22.2753
Maximiliansau - Mutterstadt BIENWD W | 11T0-0000-0376-4 | Amprion GmbH | Maximiliansau | D7MAXA2 | Mutterstadt | D7MUTT2 | 220 | - | - | - | - | - | - | - | 1360 | 1860 | 2.585 | 13.81 | 182.5 | 47.9402 | DLR values under investigation
Bixterheide - Garenfeld BIXTRH N | 11T0-0000-0272-L | Amprion GmbH | Bixterheide | D7BIXT2 | Garenfeld | D7GARE2 | 220 | - | - | - | - | - | - | - | 1221 | 1392 | 1.377 | 7.706 | 70.6 | 22.2735
Bochum - Eiberg BOCHUM W | 11T0-0000-0176-E | Amprion GmbH | Bochum | D7BOCH2 | Eiberg | D7EIBE2 | 220 | - | - | - | - | - | - | - | 1290 | 1773 | 0.735 | 3.877 | 47 | 12.8905 | DLR values under investigation
Bocklemuend - Brauweiler BOCKLE N | 11T0-0000-0194-C | Amprion GmbH | Bocklemuend | D7BOCK2 | Brauweiler | D7BRAU2 | 220 | - | - | - | - | - | - | 718 | - | - | 0.273 | 1.419 | 17.2 | 4.7177
Bocklemuend - Brauweiler BOCKLE S | 11T0-0000-0195-9 | Amprion GmbH | Bocklemuend | D7BOCK2 | Brauweiler | D7BRAU2 | 220 | - | - | - | - | - | - | 718 | - | - | 0.273 | 1.419 | 17.2 | 4.7177
Luestringen - Wehrendorf BOHMTE W | 11T0-0000-0535-D | Amprion GmbH | Luestringen | D7LUES2 | Wehrendorf | D7WEHR2 | 220 | - | - | - | - | - | - | 740 | - | - | 1.611 | 7.566 | 64.8 | 21.1442
Brauweiler - Rommerskirchen BRAUWL W | 11T0-0000-0927-S | Amprion GmbH | Brauweiler | D7BRAU1 | Rommerskirchen | D7ROKI1 | 380 | - | - | - | - | - | - | 3150 | - | - | 0.122 | 2.485 | 41.7 | 9.7208
Buerstadt - Lambsheim BUERST W | 11T0-0000-0568-T | Amprion GmbH | Buerstadt | D7BUER1 | Lambsheim | D7LAMB1 | 380 | - | - | - | - | - | - | - | 2580 | 3150 | 0.46 | 4.24 | 73.8 | 16.8921 | DLR values under investigation
Y-Buescherhof (-Karnap - Rosenblumendelle) BUESHR W | 11T0-0000-0576-V | Amprion GmbH | Buescherhof | D7BUES1 | Y-Karnap | D7YKAR1 | 380 | - | - | - | - | - | - | 2720 | - | - | 0.146 | 1.341 | 23.4 | 5.3493
Y-Karnap (-Buescherhof - Rosenblumendelle) BUESHR W | 11T0-0000-0657-V | Amprion GmbH | Karnap | D7KARN1 | Y-Karnap | D7YKAR1 | 380 | - | - | - | - | - | - | 2720 | - | - | 0.024 | 0.235 | 3.7 | 0.89044
Y-Rosenblumendelle (-Buescherhof - Karnap) BUESHR W | 11T0-0000-0838-Q | Amprion GmbH | Rosenblumendelle | D7ROSE1 | Y-Karnap | D7YKAR1 | 380 | - | - | - | - | - | - | 2720 | - | - | 0.303 | 2.847 | 47.8 | 11.1398
Brauweiler - Knapsack BURBAC O | 11T0-0000-0928-P | Amprion GmbH | Brauweiler | D7BRAU1 | Knapsack | D7KNAP1 | 380 | - | - | - | - | - | - | - | 2680 | 3150 | 0.345 | 3.197 | 55.1 | 12.6741
Y-Poeppinghausen (-Gersteinwerk - Ruhrzink) CAPPEN N | 11T0-0000-0441-Q | Amprion GmbH | Poeppinghausen | D7POEP2 | Y-Poeppinghausen | D7YPOE2 | 220 | - | - | - | - | - | - | - | 1221 | 1437 | 0.558 | 3.074 | 21.5 | 7.7632
Y-Ruhrzink (-Gersteinwerk - Poeppinghausen) CAPPEN N | 11T0-0000-0464-9 | Amprion GmbH | Ruhrzink | D7RUHR2 | Y-Poeppinghausen | D7YPOE2 | 220 | - | - | - | - | - | - | 383 | - | - | 0.088 | 0.695 | 4.8 | 1.7442
Y-Gersteinwerk (-Poeppingshausen - Ruhrzink) CAPPEN N | 11T0-0000-0280-N | Amprion GmbH | Gersteinwerk | D7GERS2 | Y-Poeppinghausen | D7YPOE2 | 220 | - | - | - | - | - | - | - | 1221 | 1392 | 1.655 | 8.937 | 110.2 | 29.968
Elmenhorst - Gersteinwerk CAPPEN S | 11T0-0000-0282-H | Amprion GmbH | Elmenhorst | D7ELME2 | Gersteinwerk | D7GERS2 | 220 | - | - | - | - | - | - | - | 1221 | 1392 | 1.509 | 8.233 | 102.2 | 27.6998
Datteln - Mengede DATTLN O | 11T0-0000-0727-1 | Amprion GmbH | Datteln | D7DATT1 | Mengede | D7MENG1 | 380 | - | - | - | - | - | - | 2720 | - | - | 0.271 | 2.562 | 42.6 | 9.9762
Datteln - Mengede DATTLN W | 11T0-0000-0728-Z | Amprion GmbH | Datteln | D7DATT1 | Mengede | D7MENG1 | 380 | - | - | - | - | - | - | 2720 | - | - | 0.271 | 2.566 | 42.6 | 9.984
Dauersberg - Linde DAURSB O | 11T0-0000-0706-C | Amprion GmbH | Dauersberg | D7DAUR1 | Linde | D7LIND1 | 380 | - | - | - | - | - | - | 2720 | - | - | 2.009 | 18.56 | 322.3 | 73.8568
Dauersberg - Halfeshof DAURSB W | 11T0-0000-0632-H | Amprion GmbH | Dauersberg | D7DAUR1 | Halfeshof | D7HALF1 | 380 | - | - | - | - | - | - | 2720 | - | - | 2.294 | 21.19 | 368.4 | 84.3717
Y-St. Huelfe (-Ohlensehlen - Wehrendorf) DUEMM S1 | 11T0-0000-0996-3 | Amprion GmbH | St. Huelfe | D7HULF1 | Y-St. Huelfe | D7YHUF1 | 380 | - | - | - | - | - | - | 481 | - | - | 0.157 | 2.988 | 57.6 | 12.5277
Y-Wehrendorf (-Ohlensehlen - St. Huelfe) DUEMM S1 | 11T0-0000-0978-5 | Amprion GmbH | Wehrendorf | D7WEHR1 | Y-St. Huelfe | D7YHUF1 | 380 | - | - | - | - | - | - | 2720 | - | - | 0.554 | 5.386 | 84.6 | 20.384
Duennwald - Opladen DUENNW O | 11T0-0000-0413-W | Amprion GmbH | Duennwald | D7DUEN2 | Opladen | D7OPLA2 | 220 | - | - | - | - | - | - | - | 1326 | 1548 | 0.593 | 3.479 | 31.4 | 9.9808
Duennwald - Opladen DUENNW W | 11T0-0000-1376-Z | Amprion GmbH | Duennwald | D7DUEN2 | Opladen | D7OPLA2 | 220 | - | - | - | - | - | - | - | 1326 | 1548 | 0.591 | 3.479 | 31.5 | 9.9966
Kusenhorst - Rosenblumendelle KUSENH | 11T0-0000-0681-0 | Amprion GmbH | Kusenhorst | D7KUSE1 | Rosenblumendelle | D7ROSE1 | 380 | - | - | - | - | - | - | 2580 | - | - | 1.13 | 10.6 | 173.7 | 40.9755
Eiberg - Karnap EIBERG N | 11T0-0000-0654-3 | Amprion GmbH | Eiberg | D7EIBE1 | Karnap | D7KARN1 | 380 | - | - | - | - | - | - | 2580 | - | - | 0.394 | 3.635 | 63 | 14.4509
Diefflen - Uchtelfangen ELLBCH N | 11T0-0000-1673-T | Amprion GmbH | Diefflen | D7DIEF2 | Uchtelfangen | D7UCHT2 | 220 | - | - | - | - | - | - | 1360 | - | - | 1.1 | 6.27 | 85.9 | 22.1616
Y-Elmenhorst (-Poeppinghausen - Ruhrzink) ELMENH S | 11T0-0000-0259-8 | Amprion GmbH | Elmenhorst | D7ELME2 | Y-Elmenhorst | D7YELM2 | 220 | - | - | - | - | - | - | - | 1221 | 1437 | 0.542 | 3.039 | 39 | 10.3961 | DLR values under investigation
Y-Poeppinghausen (-Elmenhorst - Ruhrzink) ELMENH S | 11T0-0000-0442-N | Amprion GmbH | Poeppinghausen | D7POEP2 | Y-Elmenhorst | D7YELM2 | 220 | - | - | - | - | - | - | - | 1221 | 1437 | 0.554 | 3.056 | 21.3 | 7.7044 | DLR values under investigation
Y-Ruhrzink (-Elmenhorst - Poeppinghausen) ELMENH S | 11T0-0000-0465-6 | Amprion GmbH | Ruhrzink | D7RUHR2 | Y-Elmenhorst | D7YELM2 | 220 | - | - | - | - | - | - | 334 | - | - | 0.088 | 0.695 | 4.8 | 1.7442 | DLR values under investigation
Bauler - Niederstedem ENZ N | 11T0-0000-0149-H | Amprion GmbH | Bauler | D7BAUL2 | Niederstedem | D7NSTE2 | 220 | - | - | - | - | - | - | 1920 | - | - | 0.599 | 5.75 | 80.4 | 20.5321
Bauler - Niederstedem ENZ S | 11T0-0000-0150-3 | Amprion GmbH | Bauler | D7BAUL2 | Niederstedem | D7NSTE2 | 220 | - | - | - | - | - | - | 1920 | - | - | 0.599 | 5.758 | 80.6 | 20.5719
Buescherhof - Hamborn EMSHER N | 11T0-0000-0207-Y | Amprion GmbH | Buescherhof | D7BUES2 | Hamborn | D7HAMB2 | 220 | - | - | - | - | - | - | - | 1221 | 1437 | 0.604 | 3.129 | 37.9 | 10.3991
Buescherhof - Hamborn EMSHER S | 11T0-0000-0208-V | Amprion GmbH | Buescherhof | D7BUES2 | Hamborn | D7HAMB2 | 220 | - | - | - | - | - | - | - | 1221 | 1437 | 0.603 | 3.124 | 37.9 | 10.3907
Urberach (NEU) - Urberach ERLENSEE | 11T0-0000-1382-6 | Amprion GmbH | Urberach (NEU) | D7URBN1 | Urberach | D7URBE1 | 380 | - | - | - | - | - | - | 3150 | - | - | 0.005 | 0.053 | 0.8 | 0.19663
Bischofsheim - Urberach ERZHAU N | 11T0-0000-0560-G | Amprion GmbH | Bischofsheim | D7BISC1 | Urberach | D7URBE1 | 380 | - | - | - | - | - | - | - | 2720 | 3078 | 1.271 | 12.33 | 198.4 | 47.2306
Bergmannsglueck - Buescherhof BUER S | 11T0-0000-0164-O | Amprion GmbH | Bergmannsglueck | D7BGLU2 | Buescherhof | D7BUES2 | 220 | - | - | - | - | - | - | 1290 | - | - | 0.829 | 4.941 | 67.3 | 17.4135
Duelken - Osterath FICHTH O | 11T0-0000-0230-6 | Amprion GmbH | Duelken | D7DUEL2 | Osterath | D7OSTR2 | 220 | - | - | - | - | - | - | 1282 | - | - | 1.274 | 9.071 | 143.5 | 34.4528
Edelstahl - Osterath FICHTH W | 11T0-0000-0237-M | Amprion GmbH | Edelstahl | D7EDEL2 | Osterath | D7OSTR2 | 220 | - | - | - | - | - | - | - | 1145 | 1290 | 0.481 | 2.493 | 32.8 | 8.6351
Y-St. Peter (-Reisholz - Rommerskirchen) FRIXHM S | 11T0-0000-0498-M | Amprion GmbH | St. Peter | D7PETE2 | Y-St. Peter | D7YPET2 | 220 | - | - | - | - | - | - | - | 1144 | 1548 | 0.005 | 0.05 | 0.4 | 0.13505
Y-Reisholz (-Rommerskirchen - St. Peter) FRIXHM S | 11T0-0000-0449-2 | Amprion GmbH | Reisholz | D7REIS2 | Y-St. Peter | D7YPET2 | 220 | - | - | - | - | - | - | 1290 | - | - | 0.32 | 1.754 | 90.7 | 12.0445
Y-Rommerskirchen (-Reisholz - St. Peter) FRIXHM S | 11T0-0000-0460-L | Amprion GmbH | Rommerskirchen | D7ROKI2 | Y-St. Peter | D7YPET2 | 220 | - | - | - | - | - | - | - | 1144 | 1548 | 1.048 | 5.61 | 77.7 | 19.9372
Koblenz - Limburg NASSAU | 11T0-0000-0666-U | Amprion GmbH | Koblenz | D7KOBL1 | Limburg | D7LIMB1 | 380 | - | - | - | - | - | - | 2720 | - | - | 1.429 | 13.53 | 224 | 52.5708
Y-Geithe (-Lippborg - Uentrop) GEITHE W | 11T0-0000-0608-B | Amprion GmbH | Geithe | D7GEIT1 | Y-Lippborg | D7YLPB1 | 380 | - | - | - | - | - | - | - | 2720 | 3150 | 0.091 | 0.935 | 19.5 | 4.0775
Y-Lippborg (-Geithe - Uentrop) GEITHE W | 11T0-0000-0711-N | Amprion GmbH | Lippborg | D7LIPB1 | Y-Lippborg | D7YLPB1 | 380 | - | - | - | - | - | - | 673 | - | - | 0.006 | 0.055 | 1 | 0.22395
Y-Uentrop (-Geithe - Lippborg) GEITHE W | 11T0-0000-0866-K | Amprion GmbH | Uentrop | D7UENT1 | Y-Lippborg | D7YLPB1 | 380 | - | - | - | - | - | - | - | 2580 | 3150 | 0.031 | 0.28 | 4.3 | 1.0478
Gellep - Osterath GELLEP W | 11T0-0000-0275-C | Amprion GmbH | Gellep | D7GELL2 | Osterath | D7OSTR2 | 220 | - | - | - | - | - | - | 1255 | - | - | 0.554 | 3.129 | 29.7 | 9.2056
Y-Guetersloh (-Gersteinwerk - Uentrop) GERSTE O | 11T0-0000-0943-W | Amprion GmbH | Guetersloh | D7GUET1 | Y-Gersteinwerk | D7YGER1 | 380 | - | - | - | - | - | - | 2720 | - | - | 1.181 | 10.62 | 198.8 | 43.8775
Y-Uentrop (-Gersteinwerk - Guetersloh) GERSTE O | 11T0-0000-0942-Z | Amprion GmbH | Uentrop | D7UENT1 | Y-Gersteinwerk | D7YGER1 | 380 | - | - | - | - | - | - | 2720 | - | - | 0.405 | 3.767 | 64.6 | 14.8965
Y-Gersteinwerk (-Guetersloh - Uentrop) GERSTE O | 11T0-0000-0941-1 | Amprion GmbH | Gersteinwerk | D7GERS1 | Y-Gersteinwerk | D7YGER1 | 380 | - | - | - | - | - | - | - | 2580 | 3096 | 0.363 | 3.133 | 54.2 | 12.4437 | DLR values under investigation
Niederstedem - Osburg GILZEM O | 11T0-0000-0755-W | Amprion GmbH | Niederstedem | D7NSTE1 | Osburg | D7OSBU1 | 380 | - | - | - | - | - | - | 2580 | - | - | 1.356 | 11.62 | 201.5 | 46.2074
Y-Eiberg (-Bergmannsglueck - Gelsenberg) GLADBK W | 11T0-0000-0246-L | Amprion GmbH | Eiberg | D7EIBE2 | Y-Gelsenberg | D7YGEL2 | 220 | - | - | - | - | - | - | - | 840 | 1008 | 0.924 | 5.15 | 46.1 | 14.7138 | DLR values under investigation
Y-Bergmannsglueck (-Eiberg - Gelsenberg) GLADBK W | 11T0-0000-0169-9 | Amprion GmbH | Bergmannsglueck | D7BGLU2 | Y-Gelsenberg | D7YGEL2 | 220 | - | - | - | - | - | - | 1290 | - | - | 0.434 | 2.56 | 27.1 | 7.9538
Y-Gelsenberg (-Bergmannsglueck - Eiberg) GLADBK W | 11T0-0000-0279-0 | Amprion GmbH | Gelsenberg | D7GELS2 | Y-Gelsenberg | D7YGEL2 | 220 | - | - | - | - | - | - | 700 | - | - | 0.005 | 0.05 | 0.4 | 0.13505
Y-Hanekenfaehr (-Gronau - Kusenhorst) GRAFSH W | 11T0-0000-0311-6 | Amprion GmbH | Hanekenfaehr | D7HANE2 | Y-Hanekenfaehr | D7YHAN2 | 220 | - | - | - | - | - | - | - | 1040 | 1300 | 2.45 | 20.06 | 175.6 | 56.676 | DLR values under investigation
Y-Kusenhorst (-Gronau - Hanekenfaehr) GRAFSH W | 11T0-0000-0344-M | Amprion GmbH | Kusenhorst | D7KUSE2 | Y-Hanekenfaehr | D7YHAN2 | 220 | - | - | - | - | - | - | - | 1040 | 1456 | 3.294 | 27.52 | 172.3 | 65.7564 | DLR values under investigation
Y-Gremberghoven (-Siegburg - Stockem) GREMBG O | 11T0-0000-1397-O | Amprion GmbH | Gremberghoven | D7GREM2 | Y-Stockem | D7YSTO2 | 220 | - | - | - | - | - | - | 1290 | - | - | 0.714 | 3.762 | 43.7 | 12.2439
Y-Siegburg (-Gremberghoven - Stockem) GREMBG O | 11T0-0000-1398-L | Amprion GmbH | Siegburg | D7SIEG2 | Y-Stockem | D7YSTO2 | 220 | - | - | - | - | - | - | 1290 | - | - | 0.469 | 2.523 | 31.3 | 8.486
Y-Stockem (-Gremberghoven - Siegburg) GREMBG O | 11T0-0000-1399-I | Amprion GmbH | Stockem | D7STOC2 | Y-Stockem | D7YSTO2 | 220 | - | - | - | - | - | - | 700 | - | - | 0.005 | 0.05 | 0.4 | 0.13505
Gremberghoven - Siegburg GREMBG W | 11T0-0000-1402-X | Amprion GmbH | Gremberghoven | D7GREM2 | Siegburg | D7SIEG2 | 220 | - | - | - | - | - | - | 1290 | - | - | 1.19 | 6.288 | 74.2 | 20.6267
Pfungstadt - Urberach (NEU) GRIESH O | 11T0-0000-0872-S | Amprion GmbH | Pfungstadt | D7PFUN1 | Urberach (NEU) | D7URBN1 | 380 | - | - | - | - | - | - | - | 2720 | 3150 | 0.934 | 8.773 | 150.6 | 34.7103 | DLR values under investigation
Gronau - Hanekenfaehr GRONAU W | 11T0-0000-0617-A | Amprion GmbH | Gronau | XGR_HG1 | Hanekenfaehr | D7HANE1 | 380 | - | - | - | - | - | - | - | 2580 | 3150 | 1.372 | 12.57 | 189.5 | 46.6062 | DLR values under investigation
Y-Enniger (-Guetersloh - Uentrop) GUETER S | 11T0-0000-0603-Q | Amprion GmbH | Enniger | D7ENNI1 | Y-Guetersloh | D7YGUE1 | 380 | - | - | - | - | - | - | 718 | - | - | 0.005 | 0.05 | 0.4 | 0.13505
Y-Guetersloh (-Enniger - Uentrop) GUETER S | 11T0-0000-0631-K | Amprion GmbH | Guetersloh | D7GUET1 | Y-Guetersloh | D7YGUE1 | 380 | - | - | - | - | - | - | 2565 | - | - | 0.792 | 7.143 | 134.1 | 29.5547
Y-Uentrop (-Enniger - Guetersloh) GUETER S | 11T0-0000-0867-H | Amprion GmbH | Uentrop | D7UENT1 | Y-Guetersloh | D7YGUE1 | 380 | - | - | - | - | - | - | 2565 | - | - | 0.797 | 6.966 | 124.8 | 28.156
Norf - Osterath ZONS W | 11T0-0000-0425-M | Amprion GmbH | Norf | D7NORF2 | Osterath | D7OSTR2 | 220 | - | - | - | - | - | - | - | 1290 | 1548 | 1.73 | 9.289 | 116.6 | 31.4272
Y-Kruckel (-Lippborg - Uentrop) HAARST O | 11T0-0000-0677-N | Amprion GmbH | Kruckel | D7KRUC1 | Y-Lippborg | D7YLPB1 | 380 | - | - | - | - | - | - | 3150 | - | - | 0.666 | 12.98 | 240.1 | 53.3095
Y-Lippborg (-Kruckel - Uentrop) HAARST O | 11T0-0000-0712-K | Amprion GmbH | Lippborg | D7LIPB1 | Y-Lippborg | D7YLPB1 | 380 | - | - | - | - | - | - | 769 | - | - | 0.007 | 0.07 | 1.2 | 0.27676
Y-Uentrop (-Kruckel - Lippborg) HAARST O | 11T0-0000-0868-E | Amprion GmbH | Uentrop | D7UENT1 | Y-Lippborg | D7YLPB1 | 380 | - | - | - | - | - | - | 2580 | - | - | 0.029 | 0.261 | 4.1 | 0.98783
Geithe - Unna HAARST W | 11T0-0000-0607-E | Amprion GmbH | Geithe | D7GEIT1 | Unna | D7UNNA1 | 380 | - | - | - | - | - | - | 2720 | - | - | 0.429 | 7.41 | 136 | 30.3145
St. Barbara - Mittelbexbach HAGARD O | 11T0-0000-0738-V | Amprion GmbH | St. Barbara | D7BABA1 | Mittelbexbach | D7MITB1 | 380 | - | - | - | - | - | - | 673 | - | - | 0.035 | 0.364 | 5.4 | 1.3388
St. Barbara - Mittelbexbach HAGARD W | 11T0-0000-0739-S | Amprion GmbH | St. Barbara | D7BABA1 | Mittelbexbach | D7MITB1 | 380 | - | - | - | - | - | - | 673 | - | - | 0.036 | 0.375 | 5.6 | 1.3838
Dauersberg - Setzer Wiese HELLER O | 11T0-0000-1409-C | Amprion GmbH | Dauersberg | D7DAUR2 | Setzer Wiese | D7SETZ2 | 220 | - | - | - | - | - | - | 1360 | - | - | 2.565 | 13.88 | 178.3 | 47.5053
Dauersberg - Setzer Wiese HELLER W | 11T0-0000-0480-D | Amprion GmbH | Dauersberg | D7DAUR2 | Setzer Wiese | D7SETZ2 | 220 | - | - | - | - | - | - | 1310 | - | - | 2.347 | 13.64 | 193.8 | 49.0971
Kriftel - Limburg HESSEN O | 11T0-0000-0702-O | Amprion GmbH | Kriftel | D7KRIF1 | Limburg | D7LIMB1 | 380 | - | - | - | - | - | - | 2720 | - | - | 1.558 | 14.9 | 241.6 | 57.2945
Kusenhorst - Poeppinghausen HOCHLR O | 11T0-0000-0340-Y | Amprion GmbH | Kusenhorst | D7KUSE2 | Poeppinghausen | D7POEP2 | 220 | - | - | - | - | - | - | 1290 | - | - | 1.303 | 8.266 | 104.8 | 28.106
Y-Bochum (-Kusenhorst - Poeppinghausen) HOCHLR W | 11T0-0000-0183-J | Amprion GmbH | Bochum | D7BOCH2 | Y-Poeppinghausen | D7YPOE2 | 220 | - | - | - | - | - | - | 1282 | - | - | 0.688 | 3.755 | 40.3 | 11.7471
Y-Poeppinghausen (-Bochum - Kusenhorst) HOCHLR W | 11T0-0000-0443-K | Amprion GmbH | Poeppinghausen | D7POEP2 | Y-Poeppinghausen | D7YPOE2 | 220 | - | - | - | - | - | - | 1282 | - | - | 0.619 | 3.125 | 38.9 | 10.5286
Y-Kusenhorst (-Bochum - Poeppinghausen) HOCHLR W | 11T0-0000-0345-J | Amprion GmbH | Kusenhorst | D7KUSE2 | Y-Poeppinghausen | D7YPOE2 | 220 | - | - | - | - | - | - | 1282 | - | - | 0.68 | 5.104 | 65.7 | 17.4868
Eiberg - Huellen HUELLN W | 11T0-0000-0651-C | Amprion GmbH | Eiberg | D7EIBE1 | Huellen | D7HUEL1 | 380 | - | - | - | - | - | - | - | 2580 | 3150 | 0.334 | 2.88 | 49.9 | 11.4477 | DLR values under investigation
Ibbenbueren - Westerkappeln IBBENB S | 11T0-0000-0911-D | Amprion GmbH | Ibbenbueren | D7IBBE1 | Westerkappeln | D7WEST1 | 380 | - | - | - | - | - | - | 615 | - | - | 0.343 | 3.153 | 55.4 | 12.6208
Y-Lambsheim (-Mittelbexbach - Otterbach) KAILAU N | 11T0-0000-0693-R | Amprion GmbH | Lambsheim | D7LAMB1 | Y-Otterbach | D7YOTT1 | 380 | - | - | - | - | - | - | - | 2580 | 3096 | 1.35 | 12.46 | 217.2 | 49.6776 | DLR values under investigation
Y-Mittelbexbach (-Lambsheim - Otterbach) KAILAU N | 11T0-0000-0742-8 | Amprion GmbH | Mittelbexbach | D7MITB1 | Y-Otterbach | D7YOTT1 | 380 | - | - | - | - | - | - | - | 2580 | 3096 | 1.18 | 10.06 | 174.7 | 40.0329 | DLR values under investigation
Y-Otterbach (-Lambsheim - Mittelbexbach) KAILAU N | 11T0-0000-0809-Z | Amprion GmbH | Otterbach | D7OTTE1 | Y-Otterbach | D7YOTT1 | 380 | - | - | - | - | - | - | - | 2760 | 3150 | 0.015 | 0.138 | 2.5 | 0.56089 | DLR values under investigation
Lambsheim - Otterbach KAILAU S | 11T0-0000-0688-G | Amprion GmbH | Lambsheim | D7LAMB1 | Otterbach | D7OTTE1 | 380 | - | - | - | - | - | - | - | 2580 | 3096 | 1.474 | 12.59 | 219.1 | 50.154 | DLR values under investigation
Dettingen - Urberach KARLST S | 11T0-0000-0871-V | Amprion GmbH | Dettingen | D7DETT1 | Urberach | D7URBE1 | 380 | - | - | - | - | - | - | - | 2720 | 3150 | 0.56 | 5.2 | 90.4 | 20.7041 | DLR values under investigation
Fuehlingen - Opladen KASSEL S | 11T0-0000-0414-T | Amprion GmbH | Fuehlingen | D7FUEH2 | Opladen | D7OPLA2 | 220 | - | - | - | - | - | - | 1360 | - | - | 0.257 | 1.387 | 17.9 | 4.7581
Bischofsheim - Kelsterbach KELSTB N | 11T0-0000-0658-S | Amprion GmbH | Bischofsheim | D7BISC1 | Kelsterbach | D7KELS1 | 380 | - | - | - | - | - | - | 2500 | - | - | 0.502 | 4.987 | 91.7 | 20.4209
Hattingen - Witten KEMNAD S | 11T0-0000-0915-1 | Amprion GmbH | Hattingen | D7HATT1 | Witten | D7WITT1 | 380 | - | - | - | - | - | - | - | 2580 | 3096 | 0.495 | 4.37 | 76.6 | 17.4714 | DLR values under investigation
Leupolz - Woringen KEMPTE O | 11T0-0000-0918-T | Amprion GmbH | Leupolz | D7LEUP1 | Woringen | D7WORI1 | 380 | - | - | - | - | - | - | 2760 | - | - | 0.695 | 6.702 | 116.2 | 26.6487
Oberzier - Siersdorf KIRCHB S | 11T0-0000-0776-L | Amprion GmbH | Oberzier | D7OBZI1 | Siersdorf | XSI_MB1 | 380 | - | - | - | - | - | - | - | 2720 | 3150 | 0.658 | 6.087 | 105.6 | 24.2106 | DLR values under investigation
Kruckel - Mengede KIRCHL O | 11T0-0000-0730-I | Amprion GmbH | Kruckel | D7KRUC1 | Mengede | D7MENG1 | 380 | - | - | - | - | - | - | - | 2720 | 3078 | 0.45 | 4.181 | 72.1 | 16.5798
Osterath - Rommerskirchen KNESTE W | 11T0-0000-0802-J | Amprion GmbH | Osterath | D7OSTR1 | Rommerskirchen | D7ROKI1 | 380 | - | - | - | - | - | - | 2720 | - | - | 0.828 | 7.666 | 133.9 | 30.5947
Koblenz - Weissenthurm KOBLNZ N | 11T0-0000-0897-5 | Amprion GmbH | Koblenz | D7KOBL1 | Weissenthurm | D7WTHU1 | 380 | - | - | - | - | - | - | 2580 | - | - | 0.311 | 2.714 | 47.5 | 10.8423
Hoheneck - Rheinau KUGELB O | 11T0-0000-0566-Z | Amprion GmbH | Hoheneck | D7HONE1 | Rheinau | D7REIN1 | 380 | - | - | - | - | - | - | - | 2580 | 3096 | 2.494 | 21.35 | 369.8 | 84.8504 | DLR values under investigation
Hoheneck - Rheinau KUGELB W | 11T0-0000-0567-W | Amprion GmbH | Hoheneck | D7HONE1 | Rheinau | D7REIN1 | 380 | - | - | - | - | - | - | - | 2580 | 3096 | 2.474 | 21.32 | 369.4 | 84.7449 | DLR values under investigation
Buerstadt - Rheinau KURPFA O | 11T0-0000-1421-S | Amprion GmbH | Buerstadt | D7BUER1 | Rheinau | D7REIN1 | 380 | - | - | - | - | - | - | - | 2580 | 3096 | 0.794 | 6.792 | 117.7 | 26.9997 | DLR values under investigation
Buerstadt - Rheinau KURPFA W | 11T0-0000-1422-P | Amprion GmbH | Buerstadt | D7BUER1 | Rheinau | D7REIN1 | 380 | - | - | - | - | - | - | - | 2580 | 3096 | 0.794 | 6.792 | 117.7 | 26.9997 | DLR values under investigation
Lambsheim - Weingarten LAMBSH W | 11T0-0000-0689-D | Amprion GmbH | Lambsheim | D7LAMB1 | Weingarten | D7WEIN1 | 380 | - | - | - | - | - | - | - | 2720 | 3150 | 0.866 | 7.993 | 139.5 | 31.887 | DLR values under investigation
Lechhausen - Meitingen LECHHA W | 11T0-0000-0723-D | Amprion GmbH | Lechhausen | D7LECH1 | Meitingen | D7MEIT1 | 380 | - | - | - | - | - | - | - | 1779 | 2720 | 0.841 | 7.886 | 133.2 | 30.9494
Linde - Opladen LEICHL O | 11T0-0000-0791-S | Amprion GmbH | Linde | D7LIND1 | Opladen | D7OPLA1 | 380 | - | - | - | - | - | - | - | 2720 | 3078 | 0.772 | 7.128 | 124.6 | 28.4586
Halfeshof - Opladen LEICHL W | 11T0-0000-0790-V | Amprion GmbH | Halfeshof | D7HALF1 | Opladen | D7OPLA1 | 380 | - | - | - | - | - | - | - | 2720 | 3078 | 0.46 | 4.234 | 74.2 | 16.9258
Dauersberg - Siegburg LEUSHD N | 11T0-0000-0212-8 | Amprion GmbH | Dauersberg | D7DAUR2 | Siegburg | D7SIEG2 | 220 | - | - | - | - | - | - | 1290 | - | - | 3.031 | 16.03 | 183.2 | 51.7489
Dauersberg - Siegburg LEUSHD S | 11T0-0000-0213-5 | Amprion GmbH | Dauersberg | D7DAUR2 | Siegburg | D7SIEG2 | 220 | - | - | - | - | - | - | 1290 | - | - | 3.031 | 16.03 | 183.2 | 51.7489
Liessem - Sechtem LIESSM O | 11T0-0000-0842-3 | Amprion GmbH | Liessem | D7LIES1 | Sechtem | D7SECH1 | 380 | - | - | - | - | - | - | 2580 | - | - | 0.99 | 8.81 | 150.2 | 34.7372
Spellen - Walsum LOENEN O | 11T0-0000-0491-6 | Amprion GmbH | Spellen | D7SPEL2 | Walsum | D7WALS2 | 220 | - | - | - | - | - | - | 1360 | - | - | 0.741 | 4.058 | 51.6 | 13.8182
Spellen - Walsum LOENEN W | 11T0-0000-0492-3 | Amprion GmbH | Spellen | D7SPEL2 | Walsum | D7WALS2 | 220 | - | - | - | - | - | - | 1360 | - | - | 0.744 | 4.007 | 50.7 | 13.6108
Utfort - Walsum LOHHEI W | 11T0-0000-0890-Q | Amprion GmbH | Utfort | D7UTFO1 | Walsum | D7WALS1 | 380 | - | - | - | - | - | - | 2580 | - | - | 0.271 | 2.453 | 39.3 | 9.376
Wengerrohr - Weissenthurm KONDLW | 11T0-0000-0540-O | Amprion GmbH | Wengerrohr | D7WENG2 | Weissenthurm | D7WTHU2 | 220 | - | - | - | - | - | - | - | 1221 | 1437 | 3.458 | 21.81 | 286.8 | 75.5247 | DLR values under investigation
Koblenz - Weissenthurm METTER | 11T0-0000-0898-2 | Amprion GmbH | Koblenz | D7KOBL1 | Weissenthurm | D7WTHU1 | 380 | - | - | - | - | - | - | 2580 | - | - | 0.472 | 4.534 | 68.8 | 16.8658
Sechtem - Weissenthurm MITREI | 11T0-0000-0844-Y | Amprion GmbH | Sechtem | D7SECH1 | Weissenthurm | D7WTHU1 | 380 | - | - | - | - | - | - | 2580 | - | - | 1.827 | 15.85 | 271.7 | 62.6658
Osterath - Rath MEERBU W | 11T0-0000-1498-G | Amprion GmbH | Osterath | D7OSTR1 | Rath | D7RATH1 | 380 | - | - | - | - | - | - | 646 | - | - | 0.629 | 5.908 | 99.5 | 23.1528
Gundelfingen - Meitingen MEITGN N | 11T0-0000-0721-J | Amprion GmbH | Gundelfingen | D7GUND1 | Meitingen | D7MEIT1 | 380 | - | - | - | - | - | - | 2720 | - | - | 1.081 | 9.98 | 171.1 | 39.4604
Gundelfingen - Meitingen MEITGN S | 11T0-0000-0722-G | Amprion GmbH | Gundelfingen | D7GUND1 | Meitingen | D7MEIT1 | 380 | - | - | - | - | - | - | 2720 | - | - | 1.081 | 9.98 | 171.1 | 39.4604
Gersteinwerk - Mengede MENGED N | 11T0-0000-0729-W | Amprion GmbH | Gersteinwerk | D7GERS1 | Mengede | D7MENG1 | 380 | - | - | - | - | - | - | - | 2580 | 3150 | 0.955 | 8.765 | 150.9 | 34.729 | DLR values under investigation
Lippe - Mengede MENGED S | 11T0-0000-0733-9 | Amprion GmbH | Lippe | D7LIPP1 | Mengede | D7MENG1 | 380 | - | - | - | - | - | - | - | 2720 | 3150 | 0.282 | 2.595 | 45.3 | 10.3535 | DLR values under investigation
Muendelheim - Utfort MUENDL N | 11T0-0000-0370-M | Amprion GmbH | Muendelheim | D7MUEN2 | Utfort | D7UTFO2 | 220 | - | - | - | - | - | - | - | 1360 | 1846 | 0.809 | 5.801 | 93.6 | 22.2516 | DLR values under investigation
Muendelheim - Uerdingen MUENDL S | 11T0-0000-0368-2 | Amprion GmbH | Muendelheim | D7MUEN2 | Uerdingen | D7UERD2 | 220 | - | - | - | - | - | - | 1360 | - | - | 0.477 | 2.55 | 33.6 | 8.8392
Amelsbueren - Muenster MUNSTR O | 11T0-0000-0124-3 | Amprion GmbH | Amelsbueren | D7AMEL2 | Muenster | D7MUES2 | 220 | - | - | - | - | - | - | 1004 | - | - | 0.209 | 1.081 | 12.8 | 3.5521
St. Barbara - Uchtelfangen BABARA | 11T0-0000-0506-M | Amprion GmbH | St. Barbara | D7BABA2 | Uchtelfangen | D7UCHT2 | 220 | - | - | - | - | - | - | 1290 | - | - | 1.124 | 5.896 | 77.3 | 20.3864
Hanekenfaehr - Meppen MEPPEN | 11T0-0000-0640-J | Amprion GmbH | Hanekenfaehr | D7HANE1 | Meppen | D7MEPP1 | 380 | - | - | - | - | - | - | - | 2580 | 3150 | 1.304 | 11.93 | 205.5 | 47.2822 | DLR values under investigation
Ibbenbueren - Westerkappeln NIKE S | 11T0-0000-0545-9 | Amprion GmbH | Ibbenbueren | D7IBBE2 | Westerkappeln | D7WEST2 | 220 | - | - | - | - | - | - | - | 631 | 740 | 1.181 | 5.208 | 37.6 | 13.3629
Quint - Uchtelfangen OSBURG | 11T0-0000-0445-E | Amprion GmbH | Quint | D7QUIN2 | Uchtelfangen | D7UCHT2 | 220 | - | - | - | - | - | - | - | 850 | 1523 | 3.905 | 20.86 | 273.2 | 72.089 | DLR values under investigation
Brauweiler - Rommerskirchen ROKI O | 11T0-0000-0458-1 | Amprion GmbH | Brauweiler | D7BRAU2 | Rommerskirchen | D7ROKI2 | 220 | - | - | - | - | - | - | - | 1630 | 2052 | 0.424 | 3.415 | 43.1 | 11.5852 | DLR values under investigation
Y-Leupolz (-Bidingen - Oberottmarshausen) ALLG O | 11T0-0000-0698-C | Amprion GmbH | Leupolz | D7LEUP1 | Y-Bidingen | D7BIDI1 | 380 | - | - | - | - | - | - | 2720 | - | - | 0.834 | 7.71 | 133.7 | 30.6594
Niederstedem - Rommersheim NIMSTA O | 11T0-0000-1631-E | Amprion GmbH | Niederstedem | D7NSTE1 | Rommersheim | D7ROMH1 | 380 | - | - | - | - | - | - | - | 2580 | 2770 | 1.01 | 8.7 | 150.4 | 34.5426
Niederrhein - Walsum NRHEIN W | 11T0-0000-0750-A | Amprion GmbH | Niederrhein | D7NRHE1 | Walsum | D7WALS1 | 380 | - | - | - | - | - | - | 2720 | - | - | 0.519 | 4.78 | 83.5 | 19.0778
Wehrendorf - Westerkappeln NSACHS N | 11T0-0000-0891-N | Amprion GmbH | Wehrendorf | D7WEHR1 | Westerkappeln | D7WEST1 | 380 | - | - | - | - | - | - | 2565 | - | - | 1.69 | 15.65 | 270.9 | 62.1775
Hanekenfaehr - Wehrendorf NSACHS S | 11T0-0000-0641-G | Amprion GmbH | Hanekenfaehr | D7HANE1 | Wehrendorf | D7WEHR1 | 380 | - | - | - | - | - | - | 2720 | - | - | 2.034 | 18.83 | 325.9 | 74.8064
Niederstedem - Quint NSTEDM O | 11T0-0000-0390-E | Amprion GmbH | Niederstedem | D7NSTE2 | Quint | D7QUIN2 | 220 | - | - | - | - | - | - | - | 1290 | 1773 | 1.466 | 7.745 | 99.9 | 26.5622
Niederstedem - Trier NSTEDM W | 11T0-0000-0391-B | Amprion GmbH | Niederstedem | D7NSTE2 | Trier | D7TRIE2 | 220 | - | - | - | - | - | - | 1290 | - | - | 1.285 | 6.959 | 87.6 | 23.5775
Y-Eiberg (-Ohligs - Opladen) OERKHS O | 11T0-0000-1485-T | Amprion GmbH | Eiberg | D7EIBE1 | Y-Ohligs | D7YOHL1 | 380 | - | - | - | - | - | - | - | 2580 | 3096 | 1.03 | 9.86 | 170.8 | 39.1881 | DLR values under investigation
Y-Ohligs (-Eiberg - Opladen) OERKHS O | 11T0-0000-1486-Q | Amprion GmbH | Ohligs | D7OHLI1 | Y-Ohligs | D7YOHL1 | 380 | - | - | - | - | - | - | 673 | - | - | 0.01 | 0.08 | 1.5 | 0.3308
Y-Opladen (-Eiberg - Ohligs) OERKHS O | 11T0-0000-1487-N | Amprion GmbH | Opladen | D7OPLA1 | Y-Ohligs | D7YOHL1 | 380 | - | - | - | - | - | - | 3150 | - | - | 0.47 | 4.52 | 77.5 | 17.8728
Opladen - Rommerskirchen OPLADN N | 11T0-0000-0793-M | Amprion GmbH | Opladen | D7OPLA1 | Rommerskirchen | D7ROKI1 | 380 | - | - | - | - | - | - | - | 2580 | 3150 | 0.628 | 5.582 | 97 | 22.2204
Opladen - Rommerskirchen OPLADN S | 11T0-0000-0794-J | Amprion GmbH | Opladen | D7OPLA1 | Rommerskirchen | D7ROKI1 | 380 | - | - | - | - | - | - | - | 2580 | 3150 | 0.628 | 5.585 | 97.1 | 22.2378
St. Barbara - Buerstadt OTTERB N | 11T0-0000-0203-9 | Amprion GmbH | St. Barbara | D7BABA2 | Buerstadt | D7BUER2 | 220 | - | - | - | - | - | - | - | 886 | 1282 | 6.755 | 35.33 | 445.9 | 119.8566
Y-Mutterstadt (-Homburg - Uchtelfangen) OTTERB S | 11T0-0000-1436-9 | Amprion GmbH | Mutterstadt | D7MUTT2 | Y-Homburg | D7YHOM2 | 220 | - | - | - | - | - | - | 1128 | - | - | 5.791 | 31.39 | 395.3 | 106.3728
Y-Uchtelfangen (-Homburg - Mutterstadt) OTTERB S | 11T0-0000-0505-P | Amprion GmbH | Uchtelfangen | D7UCHT2 | Y-Homburg | D7YHOM2 | 220 | - | - | - | - | - | - | 1128 | - | - | 1.763 | 9.039 | 116.9 | 31.0412
Arpe - Uentrop ARPE W | 11T0-0000-0549-Y | Amprion GmbH | Arpe | D7ARPE1 | Uentrop | D7UENT1 | 380 | - | - | - | - | - | - | 2257 | - | - | 1.991 | 17.08 | 294.7 | 67.7494
Paffendorf - Rommerskirchen PAFFEN N | 11T0-0000-0829-R | Amprion GmbH | Paffendorf | D7PAFF1 | Rommerskirchen | D7ROKI1 | 380 | - | - | - | - | - | - | - | 2580 | 3150 | 0.359 | 3.285 | 56.6 | 13.0211 | DLR values under investigation
Paffendorf - Rommerskirchen PAFFEN S | 11T0-0000-0830-D | Amprion GmbH | Paffendorf | D7PAFF1 | Rommerskirchen | D7ROKI1 | 380 | - | - | - | - | - | - | - | 2580 | 3150 | 0.359 | 3.273 | 56.8 | 13.0202 | DLR values under investigation
Kruckel - Witten PERSEBEK | 11T0-0000-0678-K | Amprion GmbH | Kruckel | D7KRUC1 | Witten | D7WITT1 | 380 | - | - | - | - | - | - | - | 2580 | 3078 | 0.252 | 2.135 | 37.9 | 8.5899
Niederrhein - Pfalzdorf PFALZD N | 11T0-0000-0385-3 | Amprion GmbH | Niederrhein | D7NRHE2 | Pfalzdorf | D7PFAL2 | 220 | - | - | - | - | - | - | 820 | - | - | 2.355 | 11.17 | 189.4 | 43.9226
Niederrhein - Pfalzdorf PFALZD S | 11T0-0000-0386-0 | Amprion GmbH | Niederrhein | D7NRHE2 | Pfalzdorf | D7PFAL2 | 220 | - | - | - | - | - | - | 820 | - | - | 2.335 | 12.28 | 173.3 | 44.0524
Y-Hattingen (-Laer - Poeppinghausen) POEPPI O | 11T0-0000-0320-5 | Amprion GmbH | Hattingen | D7HATT2 | Y-Kruckel | D7YKRC2 | 220 | - | - | - | - | - | - | 1290 | - | - | 1.054 | 5.39 | 67.2 | 18.174
Y-Laer (-Hattingen - Poeppinghausen) POEPPI O | 11T0-0000-0351-R | Amprion GmbH | Laer | D7LAER2 | Y-Kruckel | D7YKRC2 | 220 | - | - | - | - | - | - | 1290 | - | - | 0.025 | 0.13 | 1.5 | 0.42169
Y-Poeppinghausen (-Hattingen - Laer) POEPPI O | 11T0-0000-0444-H | Amprion GmbH | Poeppinghausen | D7POEP2 | Y-Kruckel | D7YKRC2 | 220 | - | - | - | - | - | - | 1290 | - | - | 0.764 | 3.853 | 48.3 | 13.027
Laer - Poeppinghausen POEPPI W | 11T0-0000-0347-D | Amprion GmbH | Laer | D7LAER2 | Poeppinghausen | D7POEP2 | 220 | - | - | - | - | - | - | 1290 | - | - | 0.746 | 3.745 | 47.2 | 12.696
Y-Kusenhorst (-Bellendorf - Bergmannsglück) POLSUM S | 11T0-0000-0346-G | Amprion GmbH | Kusenhorst | D7KUSE2 | Y-Bellendorf | D7YBEL2 | 220 | - | - | - | - | - | - | 1920 | - | - | 0.389 | 2.931 | 41.2 | 10.4937
Y-Bergmannsglueck (-Bellendorf - Kusenhorst) POLSUM S | 11T0-0000-0170-W | Amprion GmbH | Bergmannsglueck | D7BGLU2 | Y-Bellendorf | D7YBEL2 | 220 | - | - | - | - | - | - | 1920 | - | - | 0.039 | 0.373 | 5.4 | 1.3553
Benteler - Hanekenfaehr BENTLR | 11T0-0000-0307-T | Amprion GmbH | Benteler | D7BENT2 | Hanekenfaehr | D7HANE2 | 220 | - | - | - | - | - | - | 1282 | - | - | 0.073 | 0.373 | 4.6 | 1.2508
Hattingen - Laer LAER W | 11T0-0000-0314-Y | Amprion GmbH | Hattingen | D7HATT2 | Laer | D7LAER2 | 220 | - | - | - | - | - | - | 1290 | - | - | 0.916 | 5.588 | 78.3 | 19.9747
Norf - St. Peter NORF W | 11T0-0000-0496-S | Amprion GmbH | Norf | D7NORF2 | St. Peter | D7PETE2 | 220 | - | - | - | - | - | - | - | 1290 | 1548 | 0.192 | 1.05 | 11.1 | 3.2601
Opladen - St. Peter RHFELD | 11T0-0000-1671-Z | Amprion GmbH | Opladen | D7OPLA1 | St. Peter | D7PETE1 | 380 | - | - | - | - | - | - | 2580 | - | - | 0.486 | 4.398 | 74.8 | 17.3201
Niederstedem - Wengerrohr WENGER | 11T0-0000-0394-2 | Amprion GmbH | Niederstedem | D7NSTE2 | Wengerrohr | D7WENG2 | 220 | - | - | - | - | - | - | - | 1290 | 1773 | 2.37 | 11.86 | 151.3 | 40.4514
Osterath - St. Peter ZONS O | 11T0-0000-1462-9 | Amprion GmbH | Osterath | D7OSTR2 | St. Peter | D7PETE2 | 220 | - | - | - | - | - | - | 1360 | - | - | 0.758 | 7.147 | 117.8 | 27.708
Mittelbexbach - Otterbach RAMSTE S | 11T0-0000-0806-7 | Amprion GmbH | Mittelbexbach | D7MITB1 | Otterbach | D7OTTE1 | 380 | - | - | - | - | - | - | - | 2580 | 3096 | 1.194 | 10.19 | 177 | 40.5551 | DLR values under investigation
Emscherbruch - Mengede RECKLI N | 11T0-0000-1496-M | Amprion GmbH | Emscherbruch | D7EMSC1 | Mengede | D7MENG1 | 380 | - | - | - | - | - | - | - | 2580 | 3096 | 0.427 | 3.853 | 64.9 | 15.1006
Buerstadt - Hoheneck REINAU O | 11T0-0000-1669-F | Amprion GmbH | Buerstadt | D7BUER2 | Hoheneck | D7HONE2 | 220 | - | - | - | - | - | - | - | 1070 | 1282 | 6.95 | 37.39 | 399.3 | 116.6806 | DLR values under investigation
Buerstadt - Pfungstadt REINAU W | 11T0-0000-1670-1 | Amprion GmbH | Buerstadt | D7BUER2 | Pfungstadt | D7PFUN2 | 220 | - | - | - | - | - | - | 630 | - | - | 3.107 | 18.63 | 206.3 | 59.2008 | DLR values under investigation
Muendelheim - Rheinhausen RHAUSN W | 11T0-0000-0367-5 | Amprion GmbH | Muendelheim | D7MUEN2 | Rheinhausen | D7RHAU2 | 220 | - | - | - | - | - | - | - | 740 | 888 | 0.378 | 1.901 | 19.2 | 5.7692 | DLR values under investigation
Nehden - Uentrop SAUERL N | 11T0-0000-0744-2 | Amprion GmbH | Nehden | D7NEHD1 | Uentrop | D7UENT1 | 380 | - | - | - | - | - | - | 2565 | - | - | 3.381 | 29.28 | 499.7 | 115.5079
Arpe - Nehden SAUERL S | 11T0-0000-0743-5 | Amprion GmbH | Arpe | D7ARPE1 | Nehden | D7NEHD1 | 380 | - | - | - | - | - | - | 2565 | - | - | 1.498 | 12.93 | 220.8 | 51.0235
Y-Oberzier (-Paffendorf - Sechtem) SECHTM N | 11T0-0000-0781-W | Amprion GmbH | Oberzier | D7OBZI1 | Y-Paffendorf | D7YPAF1 | 380 | - | - | - | - | - | - | - | 2720 | 3150 | 0.434 | 4.009 | 70 | 15.997 | DLR values under investigation
Y-Paffendorf (-Oberzier - Sechtem) SECHTM N | 11T0-0000-0814-9 | Amprion GmbH | Paffendorf | D7PAFF1 | Y-Paffendorf | D7YPAF1 | 380 | - | - | - | - | - | - | - | 2720 | 3150 | 0.287 | 2.682 | 47.6 | 10.7896 | DLR values under investigation
Y-Sechtem (-Oberzier - Paffendorf) SECHTM N | 11T0-0000-0848-M | Amprion GmbH | Sechtem | D7SECH1 | Y-Paffendorf | D7YPAF1 | 380 | - | - | - | - | - | - | - | 2720 | 3150 | 0.789 | 7.269 | 126.9 | 29.0028 | DLR values under investigation
Y-Oberzier (-Paffendorf - Sechtem) SECHTM S | 11T0-0000-0782-T | Amprion GmbH | Oberzier | D7OBZI1 | Y-Paffendorf | D7YPAF1 | 380 | - | - | - | - | - | - | - | 2720 | 3150 | 0.434 | 4.009 | 70 | 15.997 | DLR values under investigation
Y-Paffendorf (-Oberzier - Sechtem) SECHTM S | 11T0-0000-0815-6 | Amprion GmbH | Paffendorf | D7PAFF1 | Y-Paffendorf | D7YPAF1 | 380 | - | - | - | - | - | - | - | 2720 | 3150 | 0.287 | 2.682 | 47.6 | 10.7896 | DLR values under investigation
Y-Sechtem (-Oberzier - Paffendorf) SECHTM S | 11T0-0000-0849-J | Amprion GmbH | Sechtem | D7SECH1 | Y-Paffendorf | D7YPAF1 | 380 | - | - | - | - | - | - | - | 2720 | 3150 | 0.789 | 7.3 | 126.4 | 29.0072 | DLR values under investigation
Bergmannsglueck - Niederrhein SHERMB N | 11T0-0000-0166-I | Amprion GmbH | Bergmannsglueck | D7BGLU2 | Niederrhein | D7NRHE2 | 220 | - | - | - | - | - | - | 1360 | - | - | 1.757 | 10.02 | 115.9 | 32.5422
FWH-S - Urberach SHWANH O | 11T0-0000-0516-I | Amprion GmbH | FWH-S | D7FWS 2 | Urberach | D7URBE2 | 220 | - | - | - | - | - | - | 551 | - | - | 2.597 | 12.6 | 372 | 65.3775
FWH-S - Urberach SHWANH W | 11T0-0000-0517-F | Amprion GmbH | FWH-S | D7FWS 2 | Urberach | D7URBE2 | 220 | - | - | - | - | - | - | - | 484 | 551 | 2.608 | 12.65 | 357.4 | 64.2087
Kruckel - Unna SHWERT N | 11T0-0000-0548-0 | Amprion GmbH | Kruckel | D7KRUC1 | Unna | D7UNNA1 | 380 | - | - | - | - | - | - | 3078 | - | - | 0.374 | 7.098 | 132.1 | 29.2409
Dauersberg - Sechtem SIEGTA N | 11T0-0000-0586-R | Amprion GmbH | Dauersberg | D7DAUR1 | Sechtem | D7SECH1 | 380 | - | - | - | - | - | - | 2720 | - | - | 1.86 | 17.2 | 298.2 | 68.3895
Dauersberg - Sechtem SIEGTA S | 11T0-0000-0587-O | Amprion GmbH | Dauersberg | D7DAUR1 | Sechtem | D7SECH1 | 380 | - | - | - | - | - | - | 2720 | - | - | 1.86 | 17.2 | 298.2 | 68.3895
Bacharach - Weissenthurm SOONWD O | 11T0-0000-0973-K | Amprion GmbH | Bacharach | D7BACH1 | Weissenthurm | D7WTHU1 | 380 | - | - | - | - | - | - | - | 2580 | 3096 | 1.494 | 12.62 | 218 | 50.0875 | DLR values under investigation
Waldlaubersheim - Weissenthurm SOONWD W | 11T0-0000-0901-H | Amprion GmbH | Waldlaubersheim | D7WDLA1 | Weissenthurm | D7WTHU1 | 380 | - | - | - | - | - | - | - | 2580 | 3096 | 1.911 | 16.49 | 285.2 | 65.4872 | DLR values under investigation
Niederrhein - Spellen SPELLN S | 11T0-0000-0387-Y | Amprion GmbH | Niederrhein | D7NRHE2 | Spellen | D7SPEL2 | 220 | - | - | - | - | - | - | 1360 | - | - | 0.404 | 2.17 | 28.5 | 7.5097
Osterath - Rheinhausen STRATM O | 11T0-0000-0455-A | Amprion GmbH | Osterath | D7OSTR2 | Rheinhausen | D7RHAU2 | 220 | - | - | - | - | - | - | - | 740 | 888 | 1.225 | 6.687 | 68.3 | 20.4079 | DLR values under investigation
Gellep - Muendelheim STRATM W | 11T0-0000-0364-E | Amprion GmbH | Gellep | D7GELL2 | Muendelheim | D7MUEN2 | 220 | - | - | - | - | - | - | 1290 | - | - | 0.315 | 1.655 | 21.8 | 5.7359
Norf - St. Peter STUERZ O | 11T0-0000-1445-8 | Amprion GmbH | Norf | D7NORF2 | St. Peter | D7PETE2 | 220 | - | - | - | - | - | - | 2052 | - | - | 0.096 | 0.542 | 21.8 | 3.2825
Norf - St. Peter STUERZ W | 11T0-0000-0497-P | Amprion GmbH | Norf | D7NORF2 | St. Peter | D7PETE2 | 220 | - | - | - | - | - | - | - | 1360 | 1632 | 0.172 | 0.958 | 11.7 | 3.197
Buerstadt - Pfungstadt RIED O | 11T0-0000-0816-3 | Amprion GmbH | Buerstadt | D7BUER1 | Pfungstadt | D7PFUN1 | 380 | - | - | - | - | - | - | - | 2580 | 3078 | 0.814 | 7.848 | 132.5 | 30.7935 | DLR values under investigation
Ensdorf - Uchtelfangen TAUBNT N | 11T0-0000-0604-N | Amprion GmbH | Ensdorf | D7ENSD1 | Uchtelfangen | D7UCHT1 | 380 | - | - | - | - | - | - | 2720 | - | - | 0.64 | 5.887 | 103.2 | 23.5374 | DLR values under investigation
Ensdorf - Uchtelfangen TAUBNT S | 11T0-0000-0605-K | Amprion GmbH | Ensdorf | D7ENSD1 | Uchtelfangen | D7UCHT1 | 380 | - | - | - | - | - | - | 2720 | - | - | 0.64 | 5.888 | 103.2 | 23.5394 | DLR values under investigation
Y-Osterath (-Selbeck - Utfort) TOESEE W | 11T0-0000-0805-A | Amprion GmbH | Osterath | D7OSTR1 | Y-Osterath | D7YOST1 | 380 | - | - | - | - | - | - | 2720 | - | - | 0.451 | 3.65 | 70.8 | 15.3509
Y-Selbeck (-Osterath - Utfort) TOESEE W | 11T0-0000-0851-2 | Amprion GmbH | Selbeck | D7SELB1 | Y-Osterath | D7YOST1 | 380 | - | - | - | - | - | - | 615 | - | - | 0.406 | 3.992 | 65.4 | 15.4296
Y-Utfort (-Osterath - Selbeck) TOESEE W | 11T0-0000-0880-U | Amprion GmbH | Utfort | D7UTFO1 | Y-Osterath | D7YOST1 | 380 | - | - | - | - | - | - | 2720 | - | - | 0.632 | 8.621 | 101.5 | 28.2477
Kelsterbach - Kriftel TREBUR N | 11T0-0000-0671-4 | Amprion GmbH | Kelsterbach | D7KELS1 | Kriftel | D7KRIF1 | 380 | - | - | - | - | - | - | 2500 | - | - | 0.371 | 3.547 | 70.4 | 15.09
Bischofsheim - Kriftel TREBUR S | 11T0-0000-0670-7 | Amprion GmbH | Bischofsheim | D7BISC1 | Kriftel | D7KRIF1 | 380 | - | - | - | - | - | - | 2720 | - | - | 0.515 | 5.169 | 76.1 | 18.9394
Sechtem - Siegburg TROISD O | 11T0-0000-0486-W | Amprion GmbH | Sechtem | D7SECH2 | Siegburg | D7SIEG2 | 220 | - | - | - | - | - | - | - | 1360 | 1632 | 1.004 | 5.289 | 61 | 17.1523
Sechtem - Siegburg TROISD W | 11T0-0000-0487-T | Amprion GmbH | Sechtem | D7SECH2 | Siegburg | D7SIEG2 | 220 | - | - | - | - | - | - | - | 1360 | 1632 | 1.004 | 5.317 | 60.6 | 17.1412
Osburg - Uchtelfangen UCHTLF O | 11T0-0000-0798-7 | Amprion GmbH | Osburg | D7OSBU1 | Uchtelfangen | D7UCHT1 | 380 | - | - | - | - | - | - | 2580 | - | - | 1.449 | 12.34 | 214.6 | 49.141
Niederstedem - Uchtelfangen UCHTLF W | 11T0-0000-0756-T | Amprion GmbH | Niederstedem | D7NSTE1 | Uchtelfangen | D7UCHT1 | 380 | - | - | - | - | - | - | 2580 | - | - | 2.802 | 23.99 | 415.7 | 95.3623
Y-Gersteinwerk (-Hanekenfaehr - Uentrop) UENTRO N | 11T0-0000-0616-D | Amprion GmbH | Gersteinwerk | D7GERS1 | Y-Gersteinwerk | D7YGER1 | 380 | - | - | - | - | - | - | - | 2720 | 3078 | 0.339 | 3.131 | 54.3 | 12.4512 | DLR values under investigation
Y-Hanekenfaehr (-Gersteinwerk - Uentrop) UENTRO N | 11T0-0000-0644-7 | Amprion GmbH | Hanekenfaehr | D7HANE1 | Y-Gersteinwerk | D7YGER1 | 380 | - | - | - | - | - | - | - | 2368 | 2844 | 2.891 | 26.27 | 449.9 | 103.8148 | DLR values under investigation
Y-Uentrop (-Gersteinwerk - Hanekenfaehr) UENTRO N | 11T0-0000-0869-B | Amprion GmbH | Uentrop | D7UENT1 | Y-Gersteinwerk | D7YGER1 | 380 | - | - | - | - | - | - | - | 2720 | 3078 | 0.405 | 3.767 | 64.6 | 14.8965 | DLR values under investigation
Roxel - Uentrop UENTRO S | 11T0-0000-0840-9 | Amprion GmbH | Roxel | D7ROXE1 | Uentrop | D7UENT1 | 380 | - | - | - | - | - | - | - | 2580 | 3078 | 1.656 | 14.25 | 246.7 | 56.6192
Uerdingen - Utfort UERDIN W | 11T0-0000-0113-A | Amprion GmbH | Uerdingen | D7UERD2 | Utfort | D7UTFO2 | 220 | - | - | - | - | - | - | - | 1221 | 1282 | 0.875 | 4.693 | 48.3 | 14.3771
Y-Duelken (-Edelstahl - Utfort) UTFORT W | 11T0-0000-1446-5 | Amprion GmbH | Duelken | D7DUEL2 | Y-Edelstahl | D7YEDE2 | 220 | - | - | - | - | - | - | 1360 | - | - | 0.628 | 5.761 | 100.1 | 22.9318
Y-Edelstahl (-Duelken - Utfort) UTFORT W | 11T0-0000-1447-2 | Amprion GmbH | Edelstahl | D7EDEL2 | Y-Edelstahl | D7YEDE2 | 220 | - | - | - | - | - | - | 1290 | - | - | 0.201 | 1.006 | 13.1 | 3.4666
Y-Utfort (-Duelken - Edelstahl) UTFORT W | 11T0-0000-1449-X | Amprion GmbH | Utfort | D7UTFO2 | Y-Edelstahl | D7YEDE2 | 220 | - | - | - | - | - | - | - | 841 | 1031 | 1.649 | 7.817 | 65.4 | 21.5914 | DLR values under investigation
Voehringen - Woringen VOEHRG O | 11T0-0000-0883-L | Amprion GmbH | Voehringen | D7VOEH1 | Woringen | D7WORI1 | 380 | - | - | - | - | - | - | 2760 | - | - | 1.237 | 11.93 | 207 | 47.4544
Knapsack - Sechtem WABERG W | 11T0-0000-0663-2 | Amprion GmbH | Knapsack | D7KNAP1 | Sechtem | D7SECH1 | 380 | - | - | - | - | - | - | - | 2680 | 3150 | 0.348 | 3.442 | 53.9 | 13.0068
Y-Hamborn (-Schwelgern - Walsum) WALSUM N | 11T0-0000-1455-4 | Amprion GmbH | Hamborn | D7HAMB2 | Y-Walsum | D7YWAL2 | 220 | - | - | - | - | - | - | - | 1360 | 1632 | 0.256 | 1.379 | 17.8 | 4.7311
Y-Schwelgern (-Hamborn - Walsum) WALSUM N | 11T0-0000-1456-1 | Amprion GmbH | Schwelgern | D7SHWE2 | Y-Walsum | D7YWAL2 | 220 | - | - | - | - | - | - | 700 | - | - | 0.085 | 0.464 | 5.8 | 1.5666
Y-Walsum (-Hamborn - Schwelgern) WALSUM N | 11T0-0000-1457-Z | Amprion GmbH | Walsum | D7WALS2 | Y-Walsum | D7YWAL2 | 220 | - | - | - | - | - | - | - | 1360 | 1632 | 0.088 | 0.447 | 7.9 | 1.7945
Y-Hamborn (-Schwelgern - Walsum) WALSUM S | 11T0-0000-0304-1 | Amprion GmbH | Hamborn | D7HAMB2 | Y-Schwelgern | D7YSHW2 | 220 | - | - | - | - | - | - | - | 1360 | 1632 | 0.256 | 1.379 | 17.8 | 4.7311
Y-Schwelgern (-Hamborn - Walsum) WALSUM S | 11T0-0000-0471-E | Amprion GmbH | Schwelgern | D7SHWE2 | Y-Schwelgern | D7YSHW2 | 220 | - | - | - | - | - | - | 700 | - | - | 0.099 | 0.54 | 6.8 | 1.8299
Y-Walsum (-Hamborn - Schwelgern) WALSUM S | 11T0-0000-0529-5 | Amprion GmbH | Walsum | D7WALS2 | Y-Schwelgern | D7YSHW2 | 220 | - | - | - | - | - | - | - | 1360 | 1632 | 0.083 | 0.461 | 5.5 | 1.5206
Gersteinwerk - Lippe WALTRO S | 11T0-0000-0610-V | Amprion GmbH | Gersteinwerk | D7GERS1 | Lippe | D7LIPP1 | 380 | - | - | - | - | - | - | 2720 | - | - | 0.655 | 6.073 | 104.7 | 24.0794
Gersteinwerk - Wambel WAMBEL O | 11T0-0000-0287-2 | Amprion GmbH | Gersteinwerk | D7GERS2 | Wambel | D7WAMB2 | 220 | - | - | - | - | - | - | 1290 | - | - | 1.173 | 7.896 | 90.5 | 25.527
Gersteinwerk - Wambel WAMBEL W | 11T0-0000-0289-X | Amprion GmbH | Gersteinwerk | D7GERS2 | Wambel | D7WAMB2 | 220 | - | - | - | - | - | - | 1290 | - | - | 1.172 | 7.896 | 90.4 | 25.5129
Emscherbruch - Kusenhorst WEHOLT O | 11T0-0000-1497-J | Amprion GmbH | Emscherbruch | D7EMSC1 | Kusenhorst | D7KUSE1 | 380 | - | - | - | - | - | - | - | 2370 | 2844 | 0.581 | 5.297 | 87.6 | 20.5702
Eiberg - Hattingen WEITMR W | 11T0-0000-0647-Z | Amprion GmbH | Eiberg | D7EIBE1 | Hattingen | D7HATT1 | 380 | - | - | - | - | - | - | - | 2370 | 2844 | 0.672 | 6.539 | 103.4 | 24.8306
Y-Hattingen (-Bochum - Welper) WELPER O | 11T0-0000-0321-2 | Amprion GmbH | Hattingen | D7HATT2 | Y-Welper | D7YWEL2 | 220 | - | - | - | - | - | - | 1290 | - | - | 0.158 | 1.435 | 21.7 | 5.3288
Y-Bochum (-Hattingen - Welper) WELPER O | 11T0-0000-0184-G | Amprion GmbH | Bochum | D7BOCH2 | Y-Welper | D7YWEL2 | 220 | - | - | - | - | - | - | 1290 | - | - | 0.191 | 1.852 | 28.3 | 6.9133
Y-Welper (-Bochum - Hattingen) WELPER O | 11T0-0000-0542-I | Amprion GmbH | Welper | D7WELP2 | Y-Welper | D7YWEL2 | 220 | - | - | - | - | - | - | 349 | - | - | 0.091 | 0.532 | 5.8 | 1.6774
Luestringen - Westerkappeln WESTER N | 11T0-0000-0714-E | Amprion GmbH | Luestringen | D7LUES1 | Westerkappeln | D7WEST1 | 380 | - | - | - | - | - | - | 615 | - | - | 0.495 | 4.724 | 82.9 | 18.8975
Luestringen - Westerkappeln WESTER S | 11T0-0000-0715-B | Amprion GmbH | Luestringen | D7LUES2 | Westerkappeln | D7WEST2 | 220 | - | - | - | - | - | - | 960 | - | - | 0.505 | 4.679 | 80.5 | 18.533
Y-Kusenhorst (-Huellen - Mengede) WESTFL W | 11T0-0000-0959-A | Amprion GmbH | Kusenhorst | D7KUSE1 | Y-Huellen | D7YHUE1 | 380 | - | - | - | - | - | - | - | 2580 | 3096 | 0.52 | 4.722 | 78.4 | 18.3735 | DLR values under investigation
Y-Huellen (-Kusenhorst - Mengede) WESTFL W | 11T0-0000-0960-X | Amprion GmbH | Huellen | D7HUEL1 | Y-Huellen | D7YHUE1 | 380 | - | - | - | - | - | - | - | 2580 | 3096 | 0.134 | 1.161 | 20.1 | 4.613 | DLR values under investigation
Y-Mengede (-Huellen - Kusenhorst) WESTFL W | 11T0-0000-0958-D | Amprion GmbH | Mengede | D7MENG1 | Y-Huellen | D7YHUE1 | 380 | - | - | - | - | - | - | - | 2580 | 3096 | 0.497 | 4.506 | 76.8 | 17.7643 | DLR values under investigation
Y-Dauersberg (-Asslar - Limburg) WESTW W1 | 11T0-0000-0994-9 | Amprion GmbH | Dauersberg | D7DAUR1 | Y-Dauersberg | D7YDAU1 | 380 | - | - | - | - | - | - | 2720 | - | - | 0.51 | 4.716 | 81.7 | 18.7443
Y-Limburg (-Asslar - Dauersberg) WESTW W1 | 11T0-0000-0995-6 | Amprion GmbH | Limburg | D7LIMB1 | Y-Dauersberg | D7YDAU1 | 380 | - | - | - | - | - | - | 2720 | - | - | 0.755 | 7.141 | 118.3 | 27.7551
Wehrendorf - Westerkappeln WIEHEN O | 11T0-0000-0537-7 | Amprion GmbH | Wehrendorf | D7WEHR2 | Westerkappeln | D7WEST2 | 220 | - | - | - | - | - | - | 1360 | - | - | 3.361 | 18.19 | 233.5 | 62.2345
Mengede - Witten WITTEN W | 11T0-0000-0734-6 | Amprion GmbH | Mengede | D7MENG1 | Witten | D7WITT1 | 380 | - | - | - | - | - | - | - | 2580 | 3078 | 0.72 | 6.174 | 107.2 | 24.567
Y-Buerstadt (-Bacharach - Waldlaubersheim) WONNEG O | 11T0-0000-0977-8 | Amprion GmbH | Buerstadt | D7BUER1 | Y-Waldlaubersheim | D7YWDL1 | 380 | - | - | - | - | - | - | - | 2580 | 3078 | 1.741 | 14.86 | 257.1 | 59.0244 | DLR values under investigation
Y-Bacharach (-Buerstadt - Waldlaubersheim) WONNEG O | 11T0-0000-0976-B | Amprion GmbH | Bacharach | D7BACH1 | Y-Waldlaubersheim | D7YWDL1 | 380 | - | - | - | - | - | - | - | 2580 | 3078 | 0.443 | 3.867 | 67.1 | 15.3822 | DLR values under investigation
Y-Waldlaubersheim (-Bacharach - Buerstadt) WONNEG O | 11T0-0000-0975-E | Amprion GmbH | Waldlaubersheim | D7WDLA1 | Y-Waldlaubersheim | D7YWDL1 | 380 | - | - | - | - | - | - | - | 2720 | 3078 | 0.005 | 0.05 | 0.4 | 0.13505 | DLR values under investigation
Liessem - Weissenthurm WTHURM O | 11T0-0000-0700-U | Amprion GmbH | Liessem | D7LIES1 | Weissenthurm | D7WTHU1 | 380 | - | - | - | - | - | - | 2580 | - | - | 1.246 | 10.79 | 186.8 | 42.8717
Niederrhein - Utfort ZENSEN S | 11T0-0000-1534-A | Amprion GmbH | Niederrhein | D7NRHE1 | Utfort | D7UTFO1 | 380 | - | - | - | - | - | - | 2580 | - | - | 0.79 | 7.19 | 122 | 28.2824
Y-Hoheneck (-Buers - Tiengen - Werben) BLUDNZ W | 11T0-0000-0961-U | Amprion GmbH | Hoheneck | D7HONE2 | Y-Herbertingen | D7YHBT2 | 220 | - | - | - | - | - | - | - | 540 | 1026 | 4.648 | 41.93 | 412.2 | 125.5416 | German internal tie-line; DLR values under investigation
Y-Tiengen (-Buers - Hoheneck - Werben) BLUDNZ W | 11T0-0000-0962-R | Amprion GmbH | Tiengen | D7TIEN2 | Y-Herbertingen | D7YHBT2 | 220 | - | - | - | - | - | - | 896 | - | - | 7.506 | 47.6 | 299.7 | 114.056 | German internal tie-line; DLR values under investigation
Y-Y (-Buers - Hoheneck - Tiengen - Werben) BLUDNZ W | 11T0-0000-1620-L | Amprion GmbH | Y-Werben | D73YWB2 | Y-Herbertingen | D7YHBT2 | 220 | - | - | - | - | - | - | - | - | - | 3.532 | 33.4 | 253.9 | 87.9379 | German internal tie-line
Y-Buers (-Hoheneck - Tiengen - Werben) BLUDNZ W | 11T-D4-D7-00001W | Amprion GmbH | Buers | XBR_WB2 | Y-Werben | D73YWB2 | 220 | - | - | - | - | - | - | 1710 | - | - | 0.592 | 9.08 | 70.4 | 24.1435 | German internal tie-line
Y-Buers (-Voehringen - Werben) DELLM O | 11T0-0000-0954-P | Amprion GmbH | Buers | XBR_WB2 | Y-Werben | D73YWB2 | 220 | - | - | - | - | - | - | 1710 | - | - | 0.513 | 9.13 | 69.7 | 24.0892 | German internal tie-line
Y-Dellmensingen (-Hoheneck - Voehringen) DONAU O | 11T-D4-D7-00023M | Amprion GmbH | Dellmensingen | XDE_HV1 | Y-Voehringen | D7YVOE1 | 380 | - | - | - | - | - | - | 2720 | - | - | 0.004 | 0.05 | 0.7 | 0.17865 | German internal tie-line
Y-Ohlensehlen (-St. Huelfe - Wehrendorf) DUEMM S1 | 11T0-0000-1115-Z | Amprion GmbH | Ohlensehlen | XOH_WE1 | Y-St. Huelfe | D7YHUF1 | 380 | - | - | - | - | - | - | 2616 | - | - | 0.6 | 5.34 | 93 | 21.2806 | German internal tie-line
Meitingen - Oberbachern OBACHE N | 11T-D2-D7-000504 | Amprion GmbH | Meitingen | D7MEIT1 | Oberbachern | XOB_ME1 | 380 | - | - | - | - | - | - | 2400 | - | - | 0.575 | 6.335 | 113.7 | 25.6286 | German internal tie-line
Meitingen - Oberbachern OBACHE S | 11T-D2-D7-000512 | Amprion GmbH | Meitingen | D7MEIT1 | Oberbachern | XOB_ME1 | 380 | - | - | - | - | - | - | 2400 | - | - | 0.575 | 6.335 | 113.7 | 25.6286 | German internal tie-line
Kriftel - Frankfurt TAUNUS 2 | 11T0-0000-0030-G | Amprion GmbH | Kriftel | D7KRIF1 | Frankfurt | XFR_KR1 | 380 | - | - | - | - | - | - | 2760 | - | - | 0.13 | 1.395 | 19.4 | 4.9677 | German internal tie-line
Dettingen - Grosskrotzenburg UMAIN S1 | 11T-D2-D7-00030A | Amprion GmbH | Dettingen | D7DETT1 | Grosskrotzenburg | XGK_UR1 | 380 | - | - | - | - | - | - | 2720 | - | - | 0.06 | 0.562 | 9.8 | 2.2411 | German internal tie-line
Y-Asslar (-Dauersberg - Limburg) WESTW W1 | 11T0-0000-1238-D | Amprion GmbH | Asslar | XAS_DA1 | Y-Dauersberg | D7YDAU1 | 380 | - | - | - | - | - | - | 2612 | - | - | 0.515 | 4.514 | 79.1 | 18.0443 | German internal tie-line
Dellmensingen - Voehringen DONAU W | 11T-D4-D7-00005O | Amprion GmbH | Dellmensingen | XDE_HV1 | Voehringen | D7VOEH1 | 380 | - | - | - | - | - | - | - | 2580 | 3120 | 0.247 | 2.107 | 36.7 | 8.3972 | German internal tie-line; DLR values under investigation
Meppen - Niederlangen EMSLD OW | 11T0-0000-0983-G | Amprion GmbH | Meppen | D7MEPP1 | Niederlangen | XNL_ME1 | 380 | - | - | - | - | - | - | - | 2216 | 3150 | 0.257 | 2.985 | 37.9 | 10.1569 | German internal tie-line; DLR values under investigation
Doerpen West - Hanekenfaehr EMSLD WB | 11T-D2-D7-00002F | Amprion GmbH | Doerpen West | XDO_HA1 | Hanekenfaehr | D7HANE1 | 380 | - | - | - | - | - | - | - | 2216 | 3150 | 1.105 | 10.8 | 165.2 | 40.3356 | German internal tie-line; DLR values under investigation
Daxlanden - Weingarten GERMHM S | 11T-D4-D7-00003S | Amprion GmbH | Daxlanden | XDA_MA2 | Weingarten | D7WEIN1 | 380 | - | - | - | - | - | - | - | 2720 | 3150 | 0.444 | 4.088 | 71.4 | 16.3146 | German internal tie-line; DLR values under investigation
Daxlanden - Maximiliansau GOLDGR | 11T-D4-D7-00002U | Amprion GmbH | Daxlanden | XDA_MA2 | Maximiliansau | D7MAXA2 | 220 | - | - | - | - | - | - | - | 2320 | 2784 | 0.079 | 0.729 | 12.2 | 2.8478 | German internal tie-line; DLR values under investigation
Hoheneck - Herbertingen HERBTG W | 11T0-0000-0963-O | Amprion GmbH | Hoheneck | D7HONE2 | Herbertingen | XHR_TI1 | 380 | - | - | - | - | - | - | - | 1792 | 2150 | 0.748 | 7.86 | 137.4 | 31.3817 | German internal tie-line; DLR values under investigation
Hoheneck - Pulverdingen HO PU WS | 11T-D4-D7-00014N | Amprion GmbH | Hoheneck | D7HONE2 | Pulverdingen | XPU_HO1 | 380 | - | - | - | - | - | - | 2580 | - | - | 0.132 | 1.743 | 27.2 | 6.5751 | German internal tie-line
Kuehmoos - Tiengen KUEMOS | 11T-D4-D7-00012R | Amprion GmbH | Kuehmoos | XKU_TI2 | Tiengen | D7TIEN2 | 220 | - | - | - | - | - | - | 1290 | - | - | 0.672 | 3.532 | 81.4 | 16.1918 | German internal tie-line
Bechterdissen - Guetersloh SENNE N2 | 11T0-0000-0072-V | Amprion GmbH | Bechterdissen | XBE_GU1 | Guetersloh | D7GUET1 | 380 | - | - | - | - | - | - | 2720 | - | - | 0.345 | 3.257 | 59.8 | 13.327 | German internal tie-line
Bechterdissen - Guetersloh SENNE S1 | 11T-D2-D7-00257J | Amprion GmbH | Bechterdissen | XBE_GU1 | Guetersloh | D7GUET1 | 380 | - | - | - | - | - | - | 2720 | - | - | 0.345 | 3.257 | 59.8 | 13.327 | German internal tie-line
Herbertingen - Tiengen TIENGN N | 11T-D4-D7-00010V | Amprion GmbH | Herbertingen | XHR_TI1 | Tiengen | D7TIEN1 | 380 | - | - | - | - | - | - | 1792 | - | - | 1.97 | 17.82 | 196.9 | 56.565 | German internal tie-line
Nehden - Twistetal TWIST O3 | 11T-D2-D7-00010G | Amprion GmbH | Nehden | D7NEHD1 | Twistetal | XTW_NE1 | 380 | - | - | - | - | - | - | 2580 | - | - | 0.481 | 4.296 | 72.1 | 16.8063 | German internal tie-line
Nehden - Twistetal TWIST W4 | 11T-D2-D7-00011E | Amprion GmbH | Nehden | D7NEHD1 | Twistetal | XTW_NE1 | 380 | - | - | - | - | - | - | 2580 | - | - | 0.481 | 4.295 | 72.1 | 16.8043 | German internal tie-line
Grosskrotzenburg - Urberach UMAIN N2 | 11T-D2-D7-000318 | Amprion GmbH | Grosskrotzenburg | XGK_UR1 | Urberach | D7URBE2 | 380 | - | - | - | - | - | - | 2720 | - | - | 0.322 | 2.97 | 51.7 | 11.833 | German internal tie-line
Dauersberg - Dillenburg WESTW O2 | 11T-D2-D7-00020D | Amprion GmbH | Dauersberg | D7DAUR1 | Dillenburg | XDI_DA1 | 380 | - | - | - | - | - | - | 2400 | - | - | 1.064 | 9.69 | 167.3 | 38.4487 | German internal tie-line
Y-Gohrpunkt (-Osterath - Rommerskirchen) FRIXHM N | 11T0-0000-1390-8 | Amprion GmbH | Gohrpunkt | D7OSTR2 | Y-Osterath | D7YOST2 | 220 | - | - | - | - | - | - | 2080 | - | - | 0.005 | 0.05 | 0.4 | 0.14
Y-Rommerskirchen (-Gohrpunkt - Osterath) FRIXHM N | 11T0-0000-1389-M | Amprion GmbH | Rommerskirchen | D7ROKI2 | Y-Osterath | D7YOST2 | 220 | - | - | - | - | - | - | - | 1360 | 1632 | 0.582 | 3.131 | 40.7 | 30.85
Y-Osterath (-Gohrpunkt - Rommerskirchen) FRIXHM N | 11T0-0000-1388-P | Amprion GmbH | Osterath | D7OSTR2 | Y-Osterath | D7YOST2 | 220 | - | - | - | - | - | - | - | 1360 | 1632 | 1.077 | 5.817 | 76.1 | 20.09

## Tielines
|  |  | Substation_1 |  | Substation_2 |  |  | Maximum Current Imax (A) | [6 empty] | Dynamic line rating (DLR) |  | Electrical Parameters |  |  | TSO Share until border
NE_name | EIC_Code | TSO | Full_name | Short_name | Full_name | Short_name | Voltage_level(kV) | Period 1 | Period 2 | Period 3 | Period 4 | Period 5 | Period 6 | Fixed | DLRmin(A) | DLRmax(A) | Resistance_R(Ω) | Reactance_X(Ω) | Susceptance_B(μS) | Length_(km) | Comment
Y-Werben (-Buers - Hoheneck - Tiengen) BLUDNZ W | 10T-AT-DE-00025Y | Amprion GmbH | Werben | XBR_WB2 | Y-Werben | D73YWB2 | 220 | - | - | - | - | - | - | 1472 | - | - | 0.006 | 0.05 | 0.5 | 0.15099
Y-Werben (-Buers - Voehringen) DELLM O | 10T-AT-DE-00026W | Amprion GmbH | Werben | XBR_WB2 | Y-Werben | D73YWB2 | 220 | - | - | - | - | - | - | 1540 | - | - | 0.01 | 0.059 | 0.4 | 0.1467
Westtirol - Voehringen FUESSN W | 10T1001C--00037V | Amprion GmbH | Westtirol | XWE_VO2 | Voehringen | D7VOEH2 | 220 | - | - | - | - | - | - | 1760 | - | - | 2.302 | 19.97 | 339.4 | 78.61
Ensdorf - Vigy VIGY1 N | 10T-DE-FR-00005A | Amprion GmbH | Ensdorf | D7ENSD1 | Vigy | XEN_VI1 | 380 | - | - | - | - | - | - | 2720 | - | - | 0.365 | 5.13 | 89.2 | 20.4274
Ensdorf - Vigy VIGY2 S | 10T-DE-FR-000068 | Amprion GmbH | Ensdorf | D7ENSD1 | Vigy | XEN_VI1 | 380 | - | - | - | - | - | - | 2720 | - | - | 0.365 | 5.13 | 89.2 | 20.4274
Beznau - Tiengen AARE O | 10T-CH-DE-000034 | Amprion GmbH | Beznau | XBE_TI2 | Tiengen | D7TIEN2 | 220 | 896 | 896 | 1093 | - | - | - | - | - | - | 0.245 | 1.91 | 16.2 | 5.3118
Beznau - Tiengen AARE W | 10T-CH-DE-000026 | Amprion GmbH | Beznau | XBE_TI1 | Tiengen | D7TIEN1 | 380 | 1792 | 1792 | 2187 | - | - | - | - | - | - | 0.157 | 1.707 | 18.4 | 5.3518
Oberzier - Lixhe ALEGRO | 22T201903146---W | Amprion GmbH | Oberzier | D7OBZI1 | Lixhe | XLI_OB1 | 380 | - | - | - | - | - | - | 3600 | - | - | 0.005 | 0.05 | 0.4 | 0.13505
Laufenburg - Tiengen ANDLSB | 10T-CH-DE-000131 | Amprion GmbH | Laufenburg | XLA_TI1 | Tiengen | D7TIEN1 | 380 | 1620 | 1792 | 2140 | - | - | - | - | - | - | 0.403 | 3.599 | 41.8 | 11.7125
Ensdorf - St. Avold AVOLD | 10T-DE-FR-00004C | Amprion GmbH | Ensdorf | D7ENSD2 | St. Avold | XEN_SA2 | 220 | - | - | - | - | - | - | 740 | - | - | 0.925 | 4.067 | 47.6 | 13.2865
Blooren - Trier BLO TR S | 10T-LU-DE-00002E | Amprion GmbH | Blooren | XTR_BL2 | Trier | D7TRIE2 | 220 | - | - | - | - | - | - | 1290 | - | - | 1.367 | 7.05 | 232.4 | 38.6531
Doetinchem - Niederrhein DOETM SW | 10T-DE-NL-00007J | Amprion GmbH | Doetinchem | XNR_DT1 | Niederrhein | D7NRHE2 | 380 | - | - | - | - | - | - | 3600 | - | - | 0.362 | 7.205 | 153.6 | 31.7676
Doetinchem - Niederrhein DOETM WS | 10T1001C--000235 | Amprion GmbH | Doetinchem | XNR_DT1 | Niederrhein | D7NRHE2 | 380 | - | - | - | - | - | - | 3600 | - | - | 0.48 | 7.31 | 135 | 29.9983
Bauler - Flebour FLE BA N | 10T-LU-DE-00001G | Amprion GmbH | Bauler | D7BAUL2 | Flebour | XBA_FL2 | 220 | - | - | - | - | - | - | 1290 | - | - | 0.235 | 1.512 | 19.5 | 5.1852
Bauler - Flebour FLE BA S | 10T1001C--00096F | Amprion GmbH | Bauler | D7BAUL2 | Flebour | XBA_FL2 | 220 | - | - | - | - | - | - | - | - | - | 0.235 | 1.512 | 19.5 | 5.1852
Leupolz - Westtirol FUESSN O | 10T-AT-DE-10007U | Amprion GmbH | Leupolz | D7LEUP1 | Westtirol | XWE_KE2 | 380 | - | - | - | - | - | - | 2392 | - | - | 1.219 | 10.69 | 175.3 | 41.3382
Heisdorf - Quint HEI QU N | 10T-LU-DE-00003C | Amprion GmbH | Heisdorf | XQU_HE2 | Quint | D7QUIN2 | 220 | - | - | - | - | - | - | 1290 | - | - | 1.416 | 7.3 | 97.7 | 25.5023
Gronau - Hengelo HENGL SW | 10T-DE-NL-00004P | Amprion GmbH | Gronau | D7GRON1 | Hengelo | XGR_HG1 | 380 | 2500 | 2700 |  | - | - | - | - | - | - | 0.303 | 2.907 | 47.4 | 11.2094
Gronau - Hengelo HENGL WS | 10T-DE-NL-00003R | Amprion GmbH | Gronau | D7GRON1 | Hengelo | XGR_HG1 | 380 | 2500 | 2700 |  | - | - | - | - | - | - | 0.303 | 2.907 | 47.4 | 11.2094
Maasbracht - Siersdorf SELFK SW | 10T-DE-NL-00006L | Amprion GmbH | Maasbracht | XSI_MB1 | Siersdorf | D7SIER1 | 380 | 2600 | 2655 |  | - | - | - | - | - | - | 0.495 | 4.935 | 81.6 | 19.1628
Maasbracht - Oberzier SELFK WS | 10T-DE-NL-00005N | Amprion GmbH | Maasbracht | XOB_MB1 | Oberzier | D7OBZI1 | 380 | 2600 | 2720 |  | - | - | - | - | - | - | 0.72 | 6.96 | 117.2 | 27.2734

## Transformers
Location |  |  |  | Maximum Current Imax (A) primary |  |  | Voltage_level(kV) |  | Electrical Parameters (primary) at neutral tap |  |  |  | Phase Shifting Properties
Full Name | Short Name | EIC_Code | TSO | Min | Max | Fixed | Primary | Secondary | Resistance_R(Ω) | Reactance_X(Ω) | Susceptance_B (µS) | Conductance_G (µS) | Taps used for RAO | Theta θ (°) | Symmetrical/Asymmetrical | Phase Regulation δu (%) | Angle Regulation δu (%) | Comment
Brauweiler | D7BRAU1 | 11T0-0000-1249-6 | Amprion GmbH | - | 2008 |  | 230 | 400 | 0.176 | 16.046 | -3.6 | 4.3 | - | - | - | 1.231 | -
Buerstadt | D7BUER1 | 11T0-0000-0572-6 | Amprion GmbH | - | 2008 |  | 230 | 400 | 0.247 | 16.838 | -45 | 6 | - | - | - | 1.231 | -
Buerstadt | D7BUER2 | 11T0-0000-0571-9 | Amprion GmbH | - | 1924 |  | 400 | 231 | 0.331 | 24.8 | -6.9 | 1.9 | - | -60 | - | - | 1.385
Buescherhof | D7BUES1 | 11T0-0000-0575-Y | Amprion GmbH | - | 1924 |  | 240 | 400 | 0.226 | 17.76 | -16.3 | 5.5 | - | - | - | 1.231 | -
Dauersberg | D7DAUR2 | 11T0-0000-1251-Q | Amprion GmbH | - | 1924 |  | 400 | 231 | 0.232 | 23.806 | -3 | 0.9 | - | 60 | - | - | 1.389
Dauersberg | D7DAUR2 | 11T0-0000-0589-I | Amprion GmbH | - | 1924 |  | 400 | 231 | 0.331 | 24.8 | -6.9 | 1.9 | - | 60 | - | - | 1.385
Eiberg | D7EIBE1 | 11T0-0000-0595-Q | Amprion GmbH | - | 1924 |  | 240 | 400 | 0.24 | 17.278 | -6.4 | 5.3 | - | - | - | 1.231 | -
Ensdorf | D7ENSD2 | 11T0-0000-0263-M | Amprion GmbH | - | 2008 |  | 230 | 230 | 0.089 | 10 | -3.7 | 1.1 | - | 90 | SYMM | - | 2.6
Ensdorf | D7ENSD1 | 11T0-0000-0606-H | Amprion GmbH | - | 2008 |  | 230 | 400 | 0.176 | 16.046 | -3.6 | 4.3 | - | - | - | 1.231 | -
Gersteinwerk | D7GERS1 | 11T0-0000-0614-J | Amprion GmbH | - | 2008 |  | 230 | 400 | 0.235 | 16.738 | -5.4 | 3 | - | - | - | 1.231 | -
Gersteinwerk | D7GERS1 | 11T0-0000-0615-G | Amprion GmbH | - | 2008 |  | 230 | 400 | 0.117 | 15.784 | -5.4 | 1.6 | - | - | - | 1.231 | -
Gronau | D7GRON1 | 11T0-0000-0620-R | Amprion GmbH | - | 2165 |  | 400 | 400 | 0.131 | 3.31 | -6.2 | 2.9 | -10;10 | 90 | ASYM | 1.283 | 1.111
Hanekenfähr | D7HANE1 | 11T0-0000-1278-Y | Amprion GmbH | - | 2008 |  | 230 | 400 | 0.229 | 16.483 | -11 | 5.2 | - | - | - | 1.231 | -
Hattingen | D7HATT1 | 11T0-0000-0646-1 | Amprion GmbH | - | 2008 |  | 230 | 400 | 0.235 | 16.662 | -37.3 | 3.4 | - | - | - | 1.257 | -
Hoheneck | D7HONE2 | 11T0-0000-0650-F | Amprion GmbH | - | 1271 |  | 400 | 231 | 0.558 | 25.68 | -7.6 | 1.7 | - | 60 | - | - | 1.385
Kusenhorst | D7KUSE1 | 11T0-0000-0683-V | Amprion GmbH | - | 2008 |  | 230 | 400 | 0.206 | 16.221 | -17.2 | 5.7 | - | - | - | 1.231 | -
Niederrhein | D7NRHE2 | 11T0-0000-0754-Z | Amprion GmbH | - | 1924 |  | 400 | 231 | 0.331 | 24.8 | -6.9 | 1.9 | - | 60 | - | - | 1.385
Niederstedem | D7NSTE2 | 11T0-0000-0759-K | Amprion GmbH | - | 1924 |  | 400 | 231 | 0.331 | 24.8 | -6.9 | 1.9 | - | -60 | - | - | 1.385
Niederstedem | D7NSTE2 | 11T0-0000-0758-N | Amprion GmbH | - | 1924 |  | 400 | 231 | 0.331 | 24.8 | -6.9 | 1.9 | - | -60 | - | - | 1.385
Niederstedem | D7NSTE2 | 11T0-0000-0760-6 | Amprion GmbH | - | 1155 |  | 400 | 231 | 0.459 | 45.176 | -1.6 | 0.5 | - | -60 | - | - | 0.689
Opladen | D7OPLA1 | 11T0-0000-0796-D | Amprion GmbH | - | 1924 |  | 240 | 400 | 0.24 | 17.276 | -39.1 | 6.1 | - | - | - | 1.231 | -
Opladen | D7OPLA1 | 11T0-0000-1674-Q | Amprion GmbH | - | 2008 |  | 230 | 400 | 0.176 | 16.046 | -3.6 | 4.3 |  | - | - | 1.231 | -
St. Peter | D7PETE2 | 11T0-0000-0858-I | Amprion GmbH | - | 1924 |  | 400 | 231 | 0.331 | 24.8 | -6.9 | 1.9 | - | 60 | - | - | 1.385
St. Peter | D7PETE2 | 11T0-0000-1348-4 | Amprion GmbH | - | 1924 |  | 400 | 231 | 0.331 | 24.8 | -6.9 | 1.9 | - | 60 | - | - | 1.385
Rommerskirchen | D7ROKI2 | 11T0-0000-0833-4 | Amprion GmbH | - | 1924 |  | 400 | 231 | 0.331 | 24.8 | -6.9 | 1.9 | - | 60 | - | - | 1.385
Sechtem | D7SECH1 | 11T0-0000-0847-P | Amprion GmbH | - | 1795 |  | 230 | 400 | 0.176 | 16.046 | -3.6 | 4.3 | - | - | - | 1.231 | -
Tiengen | D7TIEN2 | 11T0-0000-0859-F | Amprion GmbH | - | 1271 |  | 400 | 231 | 0.446 | 24.741 | -1 | 1.6 | - | -60 | - | - | 1.385
Uchtelfangen | D7UCHT2 | 11T0-0000-0862-W | Amprion GmbH | - | 1924 |  | 400 | 231 | 0.331 | 24.8 | -6.9 | 1.9 | - | -60 | - | - | 1.385
Urberach | D7URBE2 | 11T0-0000-0874-M | Amprion GmbH | - | 1924 |  | 400 | 231 | 0.331 | 24.8 | -6.9 | 1.9 | - | -60 | - | - | 1.385
Urberach | D7URBE2 | 11T0-0000-0875-J | Amprion GmbH | - | 1924 |  | 400 | 231 | 0.331 | 24.8 | -6.9 | 1.9 | - | -60 | - | - | 1.385
Utfort | D7UTFO2 | 11T0-0000-0879-7 | Amprion GmbH | - | 1924 |  | 400 | 231 | 0.331 | 24.8 | -6.9 | 1.9 | - | 60 | - | - | 1.385
Utfort | D7UTFO2 | 11T0-0000-0878-A | Amprion GmbH | - | 1924 |  | 400 | 231 | 0.331 | 24.8 | -6.9 | 1.9 | - | 60 | - | - | 1.385
Vöhringen | D7VOEH2 | 11T0-0000-0884-I | Amprion GmbH | - | 1924 |  | 400 | 231 | 0.232 | 23.806 | -3 | 0.9 | - | -60 | - | - | 1.389
Walsum | D7WALS1 | 11T0-0000-1352-I | Amprion GmbH | - | 2008 |  | 230 | 400 | 0.176 | 16.046 | -3.6 | 4.3 | - | - | - | 1.231 | -
Wehrendorf | D7WEHR2 | 11T0-0000-0893-H | Amprion GmbH | - | 1924 |  | 400 | 231 | 0.331 | 24.8 | -6.9 | 1.9 | - | 60 | - | - | 1.385
Westerkappeln | D7WEST1 | 11T0-0000-0914-4 | Amprion GmbH | - | 2008 |  | 230 | 400 | 0.229 | 16.482 | -28 | 4.6 | - | - | - | 1.231 | -
Weissenthurm | D7WTHU2 | 11T0-0000-0904-8 | Amprion GmbH | - | 1924 |  | 400 | 231 | 0.331 | 24.8 | -6.9 | 1.9 | - | 60 | - | - | 1.385

## Remedial Actions
Location
Name of RA | TSO | Description
PST_Gronau | Amprion GmbH | Change of tap position of phase shifting transformer (380/380) in 380kV substation Gronau

## Description
How to fill in the table:
1) Follow the description of the fields in the Static Grid Model Handbook.
2) Use the same naming convention as used for the JAO Publication Platform.
3) Most of the values are included in your IGM model.
The easiest way of gathering the data is to take your IGM and add the technical paramters from this, this is what we do at TNG; Enclosed the UCTE DEF descriptipn where to find the which data.
4) All grid elements owned by TSO from 220/380kV grid should be listed, not only the CNE.
5) Detailed description of the fields is also available below.
Lines:
|  |  | Substation 1 |  | Substation 2 |  |  | Maximum Current Imax (A) |  |  |  |  | Dynamic line rating (DLR) |  | Electrical Parameters
NE name | EIC_Code | TSO | Full name | Short name | Full name | Short name | Voltage level (kV) | Season 1 | Season 2 | Season 3 | Season 4 | Fixed | DLRmin (A) | DLRmax (A) | Resistance R (Ω) | Reactance X (Ω) | Capacity (nF) | Susceptance B(μS) | Length (km) | Comment
Name of CNE, same naming as used in the Publication database | EIC code of the CNE | Name of TSO owner, same naming as used in the Publication database | Full name as used in the publication database | 7 Characters of the uct name of the node. Wont be published, necessary for map. | Full name as used in the publication database | 7 Characters of the uct name of the node. Wont be published, necessary for map. |  | Either use seasonal limits (and define seasons in the Handbook), or use fixes values, or DLR limits | [6 empty] | Use parameters from IGM/CGM |  |  |  |  | any speciality to mention
Example:
Daxlanden - Eichstetten gn | 11TD400000588-LJ | TRANSNETBW | Daxlanden | DAXLA | Eichstetten | EICHS | 380 |  |  |  |  | 2351 | - | - | 3.621 | 31.019 | - | 542.2389 | 120.7 | none
Tielines
|  |  | Substation 1 |  | Substation 2 |  |  | Maximum Current Imax (A) |  |  |  |  | Dynamic line rating (DLR) |  | Electrical Parameters
NE name | EIC_Code | TSO | Full name | Short name | Full name | Short name | Voltage level (kV) | Summer | Interseason 1 | Interseason 2 | Winter | Fixed | DLRmin (A) | DLRmax (A) | Resistance R (Ω) | Reactance X (Ω) | Capacity (nF) | Susceptance B(μS) | Length TSO Share until border (km) | Comment
Name of CNE, same naming as used in the Publication database | EIC code of the CNE | Name of TSO owner, same naming as used in the Publication database | Full name as used in the publication database | Short Name if applicable of Substation | Full name as used in the publication database | Short Name if applicable of Substation |  | Either use seasonal limits (and define seasons in the Handbook), or use fixes values, or DLR limits | [6 empty] | Electrical paramaters should be based on the length indicated in column r, until the x-node |  |  |  | Length until border
Example:
Eichstetten - Vogelgrun ge (Kaiserstuhl) | 10T-DE-FR-00002G | TRANSNETBW | Eichstetten | EICHS | Vogelgrün | - | 220 | 2523 | - | - | 2850 | - | - | - | 0.99099 | 5.4995 | - | 1.125 | 17
Transformers
Location |  |  |  | Voltage Level U (kV) |  | Maximum Current Imax (A) primary |  | Electrical Parameters (primary) at neutral tap |  |  |  | Phase Shifting Properties
Full Name | Short Name | EIC_Code | TSO | Primary | Secondary | Min | Max | Resistance R (Ω) | Reactance X (Ω) | Conductance G (μS) | Susceptance B (μS) | Taps used for RAO | Theta θ (°) | Symmetrical/Asymmetrical | Phase Regulation δu (%) | Angle Regulation δu (%) | Comment
Same naming as used in the Publication database | Short Name | EIC code of the CNE | Name of TSO owner, same naming as used in the Publication database | Parameters from IGM | [7 empty] | Tap range absolute, that is normally send for nRAO | Parameters from IGM
Example:
PST Buers BMT37 | Bürs T37 | 11T0-0000-0082-R | TRANSNETBW | 380 | 220 | 1106 | 1106 | 0.223 | 20.064 | 3.451 | -11.215 | -10;10 | 90 | Asymmetrical | 1.14 | 1.794
Remedial Actions
Location
Name of RA | TSO | Description
Name of RA, same naming as used in the Publication database | Name of TSO owner, same naming as used in the Publication database | Short Description how the RA works
Example:
TOP_2N_EICHSTETTEN | TRANSNETBW | Opening of busbar couper in 400kV substation Eichstetten (standard case: one node operation)
FAQ
- Based on which date should we provide the static grid model? Is the current one or should we Core TSOs set out a date based on which the gird model should be given. What do you think? I based my data on the next UCTE refcase information Y-1 2021 Q1 dataset 20.01.2021 10:30
- Attached excel table
o Sheet “Line”:
What does “Short name” in column C mean? In the publication document, https://service.projectplace.com/pp/pp.cgi/r1534974061 there is no such column. Is it the nodeFrom and nodeTo? Yes this is an option or if you have internal short names, like we have 5 character names for stations that I used if from the UCTE nodes
o Sheet “Tielines:
§ Column R: “Length TSO Share until border (km)” – so this means that until the x-node, correct? indeed normally you define your impedances etc until the x-node and this should also be the basis for the length
§ I assume tielines over all borders (not only Core) need to be shared, right? yes, the static grid model should basically contain all network elements in your grid.
o Sheet”Transformer”: Column E: “Maximum Current Imax (A) primary”: What is meant by “min” (column E) and “max” (column F)? it might?!be that some TSOs have different currents for transformers, if you don’t just add the same for max and min as I did. That is coming from CWE, don’t know the reason.