## D2 70% reduction
D2 70% reduction results
|  |  | TTC (MW) | ANTC (MW) |  | LimitedBy
BD | TS | Month | Adjustment | ANTCfinal | ANTCfeasible | Adjustment | 70% Reduction (MW) | % reduction
20231016 | 2330 | October | 6100 | 936 | 408 | Minimum Margin | 528 | 56.41%
20231019 | 2330 | October | 1058 | 5156 | 558 | Minimum Margin | 4598 | 89.18%
20231104 | 1230 | November | 7410 | 682 | 498 | Minimum Margin | 184 | 26.98%
20231104 | 1330 | November | 7410 | 682 | 498 | Minimum Margin | 184 | 26.98%
20231104 | 1430 | November | 7410 | 682 | 498 | Minimum Margin | 184 | 26.98%
20231119 | 1830 | November | 9536 | 568 | 535 | Minimum Margin | 33 | 5.81%
20231119 | 1930 | November | 9536 | 568 | 535 | Minimum Margin | 33 | 5.81%
20231119 | 2030 | November | 9536 | 568 | 535 | Minimum Margin | 33 | 5.81%
20231122 | 1230 | November | 7770 | 1258 | 354 | Minimum Margin | 904 | 71.86%
20231122 | 1330 | November | 7770 | 1258 | 354 | Minimum Margin | 904 | 71.86%
20231122 | 1430 | November | 7770 | 1258 | 354 | Minimum Margin | 904 | 71.86%
20231125 | 1230 | November | 8439 | 384 | 368 | Minimum Margin | 16 | 4.167%
20231125 | 1330 | November | 8439 | 384 | 368 | Minimum Margin | 16 | 4.167%
20231125 | 1430 | November | 8439 | 384 | 368 | Minimum Margin | 16 | 4.167%
20231202 | 1530 | December | 7570 | 1052 | 370 | Minimum Margin | 682 | 64.83%
20231202 | 1630 | December | 7570 | 1052 | 370 | Minimum Margin | 682 | 64.83%
20231202 | 1730 | December | 7570 | 1052 | 370 | Minimum Margin | 682 | 64.83%
20231205 | 0930 | December | 7777 | 1320 | 214 | Minimum Margin | 1106 | 83.79%
20231205 | 1030 | December | 7777 | 1320 | 214 | Minimum Margin | 1106 | 83.79%
20231205 | 1130 | December | 7777 | 1320 | 214 | Minimum Margin | 1106 | 83.79%
20231205 | 1530 | December | 7757 | 450 | 150 | Minimum Margin | 300 | 66.67%
20231205 | 1630 | December | 7757 | 450 | 150 | Minimum Margin | 300 | 66.67%
20231205 | 1830 | December | 9000 | 2404 | 249 | Minimum Margin | 2155 | 89.64%
20231205 | 1930 | December | 9000 | 2404 | 249 | Minimum Margin | 2155 | 89.64%
20231205 | 2030 | December | 9000 | 2404 | 249 | Minimum Margin | 2155 | 89.64%

## D2 validation reduction
D2 Validation reduction results
|  |  | TTC Adjusted | TTC Validated | NTC | NTC | ANTC |  |  | LimitedBy |  | Individual Validation Reduction |  | Limiting Flags
BD | TS | Month | Adj | Validated | Border FR | Border AT | ANTCfinal | ANTCfeasible | ANTC NTC1 | Adjustment | NTC1 | Reduction TTC | Reduction TTC and 70% | TSO | Value | Reason | TSO | Value | Reason | TSO | Value | Reason
20231003 | 0030 | October | 7415 | 6877 | 2600 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 538 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231003 | 0130 | October | 7415 | 6877 | 2600 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 538 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231003 | 0230 | October | 7415 | 6877 | 2600 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 538 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231003 | 0330 | October | 7415 | 6877 | 2600 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 538 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231003 | 0430 | October | 7415 | 6877 | 2600 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 538 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231003 | 0530 | October | 7415 | 6877 | 2600 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 538 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231003 | 0630 | October | 7415 | 6877 | 2600 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 538 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231003 | 0730 | October | 7810 | 7125 | 2600 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 685 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231003 | 0830 | October | 7810 | 7125 | 2600 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 685 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231003 | 0930 | October | 7810 | 7125 | 2600 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 685 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231003 | 1030 | October | 7810 | 7125 | 2600 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 685 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231003 | 1130 | October | 7810 | 7125 | 2600 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 685 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231003 | 1230 | October | 7810 | 7125 | 2600 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 685 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231003 | 1330 | October | 7810 | 7125 | 2600 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 685 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231003 | 1430 | October | 7810 | 7125 | 2600 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 685 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231003 | 1530 | October | 7810 | 7125 | 2600 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 685 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231003 | 1630 | October | 7810 | 7125 | 2600 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 685 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231003 | 1730 | October | 8210 | 7525 | 2600 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 685 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231003 | 1830 | October | 8210 | 7525 | 2600 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 685 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231003 | 1930 | October | 8210 | 7525 | 2600 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 685 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231003 | 2030 | October | 8210 | 7525 | 2600 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 685 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231003 | 2130 | October | 8210 | 7525 | 2600 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 685 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231003 | 2230 | October | 8210 | 7525 | 2600 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 685 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231003 | 2330 | October | 7415 | 6877 | 2600 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 538 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231004 | 0730 | October | 7453 | 7419 | 2948 | 0 | -1853 | -1853 | -1819 | Critical Branch | Validation phase | 34 | 0 | FR | 2600 | Bilateral - RDCR CREY ST VULBAS 2
20231004 | 0830 | October | 7453 | 7419 | 2948 | 0 | -1853 | -1853 | -1819 | Critical Branch | Validation phase | 34 | 0 | FR | 2600 | Bilateral - RDCR CREY ST VULBAS 2
20231004 | 0930 | October | 7825 | 7630 | 3038 | 0 | -2092 | -2092 | -1897 | Critical Branch | Validation phase | 195 | 0 | FR | 2600 | Bilateral - RDCR CREY ST VULBAS 2
20231004 | 1030 | October | 7825 | 7630 | 3038 | 0 | -2092 | -2092 | -1897 | Critical Branch | Validation phase | 195 | 0 | FR | 2600 | Bilateral - RDCR CREY ST VULBAS 2
20231004 | 1130 | October | 7825 | 7630 | 3038 | 0 | -2092 | -2092 | -1897 | Critical Branch | Validation phase | 195 | 0 | FR | 2600 | Bilateral - RDCR CREY ST VULBAS 2
20231004 | 1230 | October | 7415 | 7140 | 2829 | 0 | -1695 | -1695 | -1420 | Critical Branch | Validation phase | 275 | 0 | FR | 2600 | Bilateral - RDCR CREY ST VULBAS 2
20231004 | 1330 | October | 7415 | 7140 | 2829 | 0 | -1695 | -1695 | -1420 | Critical Branch | Validation phase | 275 | 0 | FR | 2600 | Bilateral - RDCR CREY ST VULBAS 2
20231004 | 1430 | October | 7415 | 7140 | 2829 | 0 | -1695 | -1695 | -1420 | Critical Branch | Validation phase | 275 | 0 | FR | 2600 | Bilateral - RDCR CREY ST VULBAS 2
20231004 | 1530 | October | 7371 | 7164 | 2839 | 0 | -1634 | -1634 | -1427 | Critical Branch | Validation phase | 207 | 0 | FR | 2600 | Bilateral - RDCR CREY ST VULBAS 2
20231004 | 1630 | October | 7371 | 7164 | 2839 | 0 | -1634 | -1634 | -1427 | Critical Branch | Validation phase | 207 | 0 | FR | 2600 | Bilateral - RDCR CREY ST VULBAS 2
20231004 | 1730 | October | 7371 | 7164 | 2839 | 0 | -1634 | -1634 | -1427 | Critical Branch | Validation phase | 207 | 0 | FR | 2600 | Bilateral - RDCR CREY ST VULBAS 2
20231004 | 1830 | October | 6960 | 6809 | 2688 | 0 | -2107 | -2107 | -1956 | TTC Selection - LTTC | Validation phase | 151 | 0 | FR | 2600 | Bilateral - RDCR CREY ST VULBAS 2
20231004 | 1930 | October | 6960 | 6809 | 2688 | 0 | -2107 | -2107 | -1956 | TTC Selection - LTTC | Validation phase | 151 | 0 | FR | 2600 | Bilateral - RDCR CREY ST VULBAS 2
20231004 | 2030 | October | 6960 | 6809 | 2688 | 0 | -2107 | -2107 | -1956 | TTC Selection - LTTC | Validation phase | 151 | 0 | FR | 2600 | Bilateral - RDCR CREY ST VULBAS 2
20231004 | 2130 | October | 7082 | 6917 | 2734 | 0 | -1401 | -1401 | -1236 | Critical Branch | Validation phase | 165 | 0 | FR | 2600 | Bilateral - RDCR CREY ST VULBAS 2
20231004 | 2230 | October | 7082 | 6917 | 2734 | 0 | -1401 | -1401 | -1236 | Critical Branch | Validation phase | 165 | 0 | FR | 2600 | Bilateral - RDCR CREY ST VULBAS 2
20231004 | 2330 | October | 6287 | 6122 | 2551 | 0 | -565 | -565 | -400 | Critical Branch | Validation phase | 165 | 0 | FR | 2600 | Bilateral - RDCR CREY ST VULBAS 2
20231006 | 0030 | October | 7498 | 7405 | 3133 | 0 | -1602 | -1602 | -1519 | Critical Branch | Validation phase | 93 | 0 | CH | 7135 | Missing CNEC in CC: CNE: 380kV Gorlago - Robbia , C: N-2 ALBERTVILLE-RONDISSONE
20231006 | 0130 | October | 7498 | 7405 | 3133 | 0 | -1602 | -1602 | -1519 | Critical Branch | Validation phase | 93 | 0 | CH | 7135 | Missing CNEC in CC: CNE: 380kV Gorlago - Robbia , C: N-2 ALBERTVILLE-RONDISSONE
20231006 | 0230 | October | 7498 | 7405 | 3133 | 0 | -1602 | -1602 | -1519 | Critical Branch | Validation phase | 93 | 0 | CH | 7135 | Missing CNEC in CC: CNE: 380kV Gorlago - Robbia , C: N-2 ALBERTVILLE-RONDISSONE
20231006 | 0330 | October | 7201 | 6880 | 2895 | 0 | -2729 | -2729 | -2416 | Critical Branch | Validation phase | 321 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | CH | 6616 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 ALBERTVILLE-RONDISSONE
20231006 | 0430 | October | 7201 | 6880 | 2895 | 0 | -2729 | -2729 | -2416 | Critical Branch | Validation phase | 321 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | CH | 6616 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 ALBERTVILLE-RONDISSONE
20231006 | 0530 | October | 7201 | 6880 | 2895 | 0 | -2729 | -2729 | -2416 | Critical Branch | Validation phase | 321 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | CH | 6616 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 ALBERTVILLE-RONDISSONE
20231006 | 0630 | October | 7201 | 6880 | 2895 | 0 | -2729 | -2729 | -2416 | Critical Branch | Validation phase | 321 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | CH | 6616 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 ALBERTVILLE-RONDISSONE
20231006 | 0730 | October | 7913 | 7886 | 3147 | 0 | -2831 | -2831 | -2808 | Critical Branch | Validation phase | 27 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | CH | 7615 | Missing CNEC in CC: CNE: 380kV Gorlago - Robbia , C: N-2 ALBERTVILLE-RONDISSONE
20231006 | 0830 | October | 7913 | 7886 | 3147 | 0 | -2831 | -2831 | -2808 | Critical Branch | Validation phase | 27 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | CH | 7615 | Missing CNEC in CC: CNE: 380kV Gorlago - Robbia , C: N-2 ALBERTVILLE-RONDISSONE
20231006 | 0930 | October | 6960 | 6946 | 2746 | 0 | -3122 | -3122 | -3071 | TTC Selection - LTTC | TTC Selection - LTTC | 14 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231006 | 1030 | October | 6960 | 6946 | 2746 | 0 | -3122 | -3122 | -3071 | TTC Selection - LTTC | TTC Selection - LTTC | 14 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231006 | 1130 | October | 6960 | 6946 | 2746 | 0 | -3122 | -3122 | -3071 | TTC Selection - LTTC | TTC Selection - LTTC | 14 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231006 | 1230 | October | 7007 | 6994 | 2767 | 0 | -2187 | -2187 | -2191 | Critical Branch | Critical Branch | 13 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231006 | 1330 | October | 7007 | 6994 | 2767 | 0 | -2187 | -2187 | -2191 | Critical Branch | Critical Branch | 13 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231006 | 1430 | October | 7007 | 6994 | 2767 | 0 | -2187 | -2187 | -2191 | Critical Branch | Critical Branch | 13 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231006 | 1530 | October | 7170 | 7158 | 2837 | 0 | -2473 | -2473 | -2465 | Critical Branch | Critical Branch | 12 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231006 | 1630 | October | 7170 | 7158 | 2837 | 0 | -2473 | -2473 | -2465 | Critical Branch | Critical Branch | 12 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231006 | 1730 | October | 7170 | 7158 | 2837 | 0 | -2473 | -2473 | -2465 | Critical Branch | Critical Branch | 12 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231006 | 1830 | October | 8669 | 8658 | 3476 | 0 | -4897 | -4897 | -4892 | Critical Branch | Smoothing ramp | 11 | 0 | Smoothing
20231007 | 0030 | October | 7873 | 7415 | 3138 | 0 | -4619 | -4619 | -4138 | Critical Branch | Validation phase | 458 | 0 | CH | 7145 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20231007 | 0130 | October | 7873 | 7415 | 3138 | 0 | -4619 | -4619 | -4138 | Critical Branch | Validation phase | 458 | 0 | CH | 7145 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20231007 | 0230 | October | 7873 | 7415 | 3138 | 0 | -4619 | -4619 | -4138 | Critical Branch | Validation phase | 458 | 0 | CH | 7145 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20231007 | 0330 | October | 7537 | 7415 | 3138 | 0 | -4537 | -4537 | -4393 | Critical Branch | Validation phase | 122 | 0 | CH | 7145 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20231007 | 0430 | October | 7537 | 7415 | 3138 | 0 | -4537 | -4537 | -4393 | Critical Branch | Validation phase | 122 | 0 | CH | 7145 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20231007 | 0530 | October | 7537 | 7415 | 3138 | 0 | -4537 | -4537 | -4393 | Critical Branch | Validation phase | 122 | 0 | CH | 7145 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20231007 | 0630 | October | 7537 | 7415 | 3138 | 0 | -4537 | -4537 | -4393 | Critical Branch | Validation phase | 122 | 0 | CH | 7145 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20231007 | 1830 | October | 7701 | 7415 | 2942 | 9 | -2101 | -2101 | -1818 | Critical Branch | Validation phase | 286 | 0 | CH | 7140 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20231007 | 1930 | October | 7701 | 7415 | 2942 | 9 | -2101 | -2101 | -1818 | Critical Branch | Validation phase | 286 | 0 | CH | 7140 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20231007 | 2030 | October | 7701 | 7415 | 2942 | 9 | -2101 | -2101 | -1818 | Critical Branch | Validation phase | 286 | 0 | CH | 7140 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20231007 | 2130 | October | 8062 | 7415 | 2942 | 9 | -1930 | -1930 | -1287 | Critical Branch | Validation phase | 647 | 0 | CH | 7140 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20231007 | 2230 | October | 8062 | 7415 | 2942 | 9 | -1930 | -1930 | -1287 | Critical Branch | Validation phase | 647 | 0 | CH | 7140 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20231008 | 0930 | October | 7953 | 7877 | 3348 | 0 | -3085 | -3085 | -3009 | Critical Branch | Validation phase | 76 | 0 | CH | 7687 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 ALBERTVILLE-RONDISSONE
20231008 | 1030 | October | 7953 | 7877 | 3348 | 0 | -3085 | -3085 | -3009 | Critical Branch | Validation phase | 76 | 0 | CH | 7687 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 ALBERTVILLE-RONDISSONE
20231008 | 1130 | October | 7953 | 7877 | 3348 | 0 | -3085 | -3085 | -3009 | Critical Branch | Validation phase | 76 | 0 | CH | 7687 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 ALBERTVILLE-RONDISSONE
20231008 | 1830 | October | 7691 | 7596 | 3220 | 0 | -2608 | -2608 | -2513 | Critical Branch | Validation phase | 95 | 0 | CH | 7406 | Expected overloading on the following CNEC: CNE: 380kV Gorlago - Robbia , C: N-1 SOAZZA-BULCIAGO
20231008 | 1930 | October | 7691 | 7596 | 3220 | 0 | -2608 | -2608 | -2513 | Critical Branch | Validation phase | 95 | 0 | CH | 7406 | Expected overloading on the following CNEC: CNE: 380kV Gorlago - Robbia , C: N-1 SOAZZA-BULCIAGO
20231008 | 2030 | October | 7691 | 7596 | 3220 | 0 | -2608 | -2608 | -2513 | Critical Branch | Validation phase | 95 | 0 | CH | 7406 | Expected overloading on the following CNEC: CNE: 380kV Gorlago - Robbia , C: N-1 SOAZZA-BULCIAGO
20231009 | 0030 | October | 7821 | 6815 | 2866 | 0 | -2499 | -2499 | -1506 | Critical Branch | Validation phase | 1006 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | CH | 6552 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231009 | 0130 | October | 7821 | 6815 | 2866 | 0 | -2499 | -2499 | -1506 | Critical Branch | Validation phase | 1006 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | CH | 6552 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231009 | 0230 | October | 7821 | 6815 | 2866 | 0 | -2499 | -2499 | -1506 | Critical Branch | Validation phase | 1006 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | CH | 6552 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231009 | 0730 | October | 8019 | 8017 | 3203 | 0 | -3331 | -3331 | -3340 | Critical Branch | Critical Branch | 2 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231009 | 0830 | October | 7719 | 7717 | 3199 | 0 | -3013 | -3013 | -3023 | Critical Branch | Critical Branch | 2 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231009 | 0930 | October | 8117 | 7747 | 3213 | 0 | -1257 | -1257 | -920 | Critical Branch | Validation phase | 370 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | CH | 7474 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 RONDISSONE-TRINO
20231009 | 1030 | October | 8117 | 7747 | 3213 | 0 | -1257 | -1257 | -920 | Critical Branch | Validation phase | 370 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | CH | 7474 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 RONDISSONE-TRINO
20231009 | 1130 | October | 8117 | 7747 | 3213 | 0 | -1257 | -1257 | -920 | Critical Branch | Validation phase | 370 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | CH | 7474 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 RONDISSONE-TRINO
20231009 | 1230 | October | 7859 | 7786 | 3230 | 0 | -2431 | -2431 | -2355 | Critical Branch | Validation phase | 73 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | CH | 7512 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza , C: N-2 Pradella-Robbia + Filisur-Robbia
20231009 | 1330 | October | 7859 | 7786 | 3230 | 0 | -2431 | -2431 | -2355 | Critical Branch | Validation phase | 73 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | CH | 7512 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza , C: N-2 Pradella-Robbia + Filisur-Robbia
20231009 | 1430 | October | 7859 | 7786 | 3230 | 0 | -2431 | -2431 | -2355 | Critical Branch | Validation phase | 73 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | CH | 7512 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza , C: N-2 Pradella-Robbia + Filisur-Robbia
20231009 | 1530 | October | 7740 | 7318 | 3023 | 0 | -3195 | -3195 | -2786 | Critical Branch | Validation phase | 422 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | IT | 7050 | ABV-GRA1/2 on ABV-GRA3 and RON-ABV 1/2 on 220 kV grid
20231009 | 1630 | October | 7740 | 7318 | 3023 | 0 | -3195 | -3195 | -2786 | Critical Branch | Validation phase | 422 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | IT | 7050 | ABV-GRA1/2 on ABV-GRA3 and RON-ABV 1/2 on 220 kV grid
20231009 | 1730 | October | 7740 | 7318 | 3023 | 0 | -3195 | -3195 | -2786 | Critical Branch | Validation phase | 422 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | IT | 7050 | ABV-GRA1/2 on ABV-GRA3 and RON-ABV 1/2 on 220 kV grid
20231009 | 1830 | October | 7420 | 7318 | 3023 | 0 | -2740 | -2740 | -2640 | Critical Branch | Validation phase | 102 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | IT | 7050 | ABV-GRA1/2 on ABV-GRA3 and RON-ABV 1/2 on 220 kV grid
20231009 | 1930 | October | 7420 | 7318 | 3023 | 0 | -2740 | -2740 | -2640 | Critical Branch | Validation phase | 102 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | IT | 7050 | ABV-GRA1/2 on ABV-GRA3 and RON-ABV 1/2 on 220 kV grid
20231009 | 2030 | October | 7420 | 7318 | 3023 | 0 | -2740 | -2740 | -2640 | Critical Branch | Validation phase | 102 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | IT | 7050 | ABV-GRA1/2 on ABV-GRA3 and RON-ABV 1/2 on 220 kV grid
20231009 | 2130 | October | 7851 | 7318 | 3023 | 0 | -2116 | -2116 | -1590 | Critical Branch | Validation phase | 533 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | IT | 7050 | ABV-GRA1/2 on ABV-GRA3 and RON-ABV 1/2 on 220 kV grid
20231009 | 2230 | October | 7851 | 7318 | 3023 | 0 | -2116 | -2116 | -1590 | Critical Branch | Validation phase | 533 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | IT | 7050 | ABV-GRA1/2 on ABV-GRA3 and RON-ABV 1/2 on 220 kV grid
20231009 | 2330 | October | 7056 | 6961 | 3065 | 0 | -1270 | -1270 | -1182 | Critical Branch | Validation phase | 95 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | CH | 6693 | Missing CNEC in CC: CNE: 380kV Gorlago - Robbia , C: 380KV SILS-SOAZZA
20231010 | 0030 | October | 7692 | 7380 | 3264 | 0 | -2003 | -2003 | -1705 | Critical Branch | Validation phase | 312 | 0 | CH | 7110 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231010 | 0130 | October | 7692 | 7380 | 3264 | 0 | -2003 | -2003 | -1705 | Critical Branch | Validation phase | 312 | 0 | CH | 7110 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231010 | 0230 | October | 7692 | 7380 | 3264 | 0 | -2003 | -2003 | -1705 | Critical Branch | Validation phase | 312 | 0 | CH | 7110 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231010 | 0730 | October | 7900 | 7698 | 3191 | 0 | -2462 | -2462 | -2274 | Critical Branch | Validation phase | 202 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | IT | 7425 | N-2 ABV-RON 1 and 2 on VNS-VLR(103%)
20231010 | 0830 | October | 7900 | 7698 | 3191 | 0 | -2462 | -2462 | -2274 | Critical Branch | Validation phase | 202 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | IT | 7425 | N-2 ABV-RON 1 and 2 on VNS-VLR(103%)
20231010 | 0930 | October | 7153 | 7144 | 2945 | 0 | -2540 | -2540 | -2545 | Critical Branch | Critical Branch | 9 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231010 | 1030 | October | 7153 | 7144 | 2945 | 0 | -2540 | -2540 | -2545 | Critical Branch | Critical Branch | 9 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231010 | 1130 | October | 7153 | 7144 | 2945 | 0 | -2540 | -2540 | -2545 | Critical Branch | Critical Branch | 9 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231010 | 1230 | October | 6660 | 6318 | 2579 | 0 | -3239 | -3239 | -2906 | TTC Selection - LTTC | Validation phase | 342 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | CH | 6061 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231010 | 1330 | October | 6660 | 6318 | 2579 | 0 | -3239 | -3239 | -2906 | TTC Selection - LTTC | Validation phase | 342 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | CH | 6061 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231010 | 1430 | October | 6660 | 6318 | 2579 | 0 | -3239 | -3239 | -2906 | TTC Selection - LTTC | Validation phase | 342 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | CH | 6061 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231010 | 1530 | October | 6956 | 5333 | 2143 | 0 | -3963 | -3963 | -2350 | Critical Branch | Validation phase | 1623 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | CH | 5088 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231010 | 1630 | October | 6956 | 5333 | 2143 | 0 | -3963 | -3963 | -2350 | Critical Branch | Validation phase | 1623 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | CH | 5088 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231010 | 1730 | October | 6956 | 5333 | 2143 | 0 | -3963 | -3963 | -2350 | Critical Branch | Validation phase | 1623 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | CH | 5088 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231010 | 1830 | October | 7700 | 6833 | 2803 | 10 | -2704 | -2704 | -1849 | Critical Branch | Smoothing ramp | 867 | 0 | Smoothing
20231010 | 1930 | October | 7700 | 7698 | 3191 | 0 | -2704 | -2704 | -2714 | Critical Branch | Critical Branch | 2 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231010 | 2030 | October | 7700 | 7698 | 3191 | 0 | -2704 | -2704 | -2714 | Critical Branch | Critical Branch | 2 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231011 | 0030 | October | 7525 | 6105 | 2600 | 0 | -3142 | -3142 | -1699 | Critical Branch | Validation phase | 1420 | 0 | FR | 2600 | Bilateral - Problèmes de coordination avec TERNA |  |  |  | CH | 6027 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231011 | 0130 | October | 7525 | 6105 | 2600 | 0 | -3142 | -3142 | -1699 | Critical Branch | Validation phase | 1420 | 0 | FR | 2600 | Bilateral - Problèmes de coordination avec TERNA |  |  |  | CH | 6027 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231011 | 0230 | October | 7525 | 6105 | 2600 | 0 | -3142 | -3142 | -1699 | Critical Branch | Validation phase | 1420 | 0 | FR | 2600 | Bilateral - Problèmes de coordination avec TERNA |  |  |  | CH | 6027 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231011 | 0330 | October | 6801 | 6412 | 2600 | 0 | -4142 | -4142 | -3718 | Critical Branch | Critical Branch | 389 | 0 | FR | 2600 | Bilateral - Problèmes de coordination avec TERNA
20231011 | 0430 | October | 6801 | 6412 | 2600 | 0 | -4142 | -4142 | -3718 | Critical Branch | Critical Branch | 389 | 0 | FR | 2600 | Bilateral - Problèmes de coordination avec TERNA
20231011 | 0530 | October | 6801 | 6412 | 2600 | 0 | -4142 | -4142 | -3718 | Critical Branch | Critical Branch | 389 | 0 | FR | 2600 | Bilateral - Problèmes de coordination avec TERNA
20231011 | 0630 | October | 6801 | 6412 | 2600 | 0 | -4142 | -4142 | -3718 | Critical Branch | Critical Branch | 389 | 0 | FR | 2600 | Bilateral - Problèmes de coordination avec TERNA
20231011 | 0730 | October | 7018 | 6728 | 2600 | 0 | -2913 | -2913 | -2578 | Critical Branch | Critical Branch | 290 | 0 | FR | 2600 | Bilateral - Problèmes de coordination avec TERNA
20231011 | 0830 | October | 7018 | 6728 | 2600 | 0 | -2913 | -2913 | -2578 | Critical Branch | Critical Branch | 290 | 0 | FR | 2600 | Bilateral - Problèmes de coordination avec TERNA
20231011 | 0930 | October | 7847 | 6383 | 2600 | 0 | -3995 | -3995 | -2528 | Critical Branch | Validation phase | 1464 | 0 | FR | 2600 | Bilateral - Problèmes de coordination avec TERNA |  |  |  | CH | 6207 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231011 | 1030 | October | 7847 | 6383 | 2600 | 0 | -3995 | -3995 | -2528 | Critical Branch | Validation phase | 1464 | 0 | FR | 2600 | Bilateral - Problèmes de coordination avec TERNA |  |  |  | CH | 6207 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231011 | 1130 | October | 7847 | 6383 | 2600 | 0 | -3995 | -3995 | -2528 | Critical Branch | Validation phase | 1464 | 0 | FR | 2600 | Bilateral - Problèmes de coordination avec TERNA |  |  |  | CH | 6207 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231011 | 1230 | October | 7134 | 6748 | 2600 | 0 | -2596 | -2596 | -2159 | Critical Branch | Validation phase | 386 | 0 | FR | 2600 | Bilateral - Problèmes de coordination avec TERNA |  |  |  | CH | 6864 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231011 | 1330 | October | 7134 | 6748 | 2600 | 0 | -2596 | -2596 | -2159 | Critical Branch | Validation phase | 386 | 0 | FR | 2600 | Bilateral - Problèmes de coordination avec TERNA |  |  |  | CH | 6864 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231011 | 1430 | October | 7134 | 6748 | 2600 | 0 | -2596 | -2596 | -2159 | Critical Branch | Validation phase | 386 | 0 | FR | 2600 | Bilateral - Problèmes de coordination avec TERNA |  |  |  | CH | 6864 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231011 | 1530 | October | 7110 | 6780 | 2600 | 0 | -3379 | -3379 | -3003 | Critical Branch | Critical Branch | 330 | 0 | FR | 2600 | Bilateral - Problèmes de coordination avec TERNA
20231011 | 1630 | October | 7410 | 7066 | 2600 | 0 | -3656 | -3656 | -3264 | Critical Branch | Critical Branch | 344 | 0 | FR | 2600 | Bilateral - Problèmes de coordination avec TERNA
20231011 | 1730 | October | 7410 | 7066 | 2600 | 0 | -3656 | -3656 | -3264 | Critical Branch | Critical Branch | 344 | 0 | FR | 2600 | Bilateral - Problèmes de coordination avec TERNA
20231011 | 1830 | October | 7342 | 6542 | 2574 | 0 | -3370 | -3370 | -2570 | Critical Branch | Validation phase | 800 | 0 | CH | 6352 | Expected overloading on the following CNEC: CNE: 380kV Gorlago - Robbia , C: N-1 SOAZZA-BULCIAGO
20231011 | 1930 | October | 7342 | 6542 | 2574 | 0 | -3370 | -3370 | -2570 | Critical Branch | Validation phase | 800 | 0 | CH | 6352 | Expected overloading on the following CNEC: CNE: 380kV Gorlago - Robbia , C: N-1 SOAZZA-BULCIAGO
20231011 | 2030 | October | 7342 | 6542 | 2574 | 0 | -3370 | -3370 | -2570 | Critical Branch | Validation phase | 800 | 0 | CH | 6352 | Expected overloading on the following CNEC: CNE: 380kV Gorlago - Robbia , C: N-1 SOAZZA-BULCIAGO
20231011 | 2130 | October | 7357 | 6539 | 2573 | 0 | -741 | -741 | 77 | Critical Branch | Validation phase | 818 | 77 | CH | 6349 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231011 | 2230 | October | 7357 | 6539 | 2573 | 0 | -741 | -741 | 77 | Critical Branch | Validation phase | 818 | 77 | CH | 6349 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231011 | 2330 | October | 6671 | 5853 | 2429 | 0 | 109 | 109 | 818 | Minimum Margin | Validation phase | 818 | 818 | CH | 5663 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231012 | 0030 | October | 7522 | 6935 | 2600 | 0 | -3273 | -3273 | -2588 | Critical Branch | Critical Branch | 587 | 0 | FR | 2600 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/ALBERTVILLE G.ILE 3 | AT | 0 | Reduction because ot disconnection of line 912 and 261
20231012 | 0130 | October | 7522 | 6935 | 2600 | 0 | -3273 | -3273 | -2588 | Critical Branch | Critical Branch | 587 | 0 | FR | 2600 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/ALBERTVILLE G.ILE 3 | AT | 0 | Reduction because ot disconnection of line 912 and 261
20231012 | 0230 | October | 7522 | 6935 | 2600 | 0 | -3273 | -3273 | -2588 | Critical Branch | Critical Branch | 587 | 0 | FR | 2600 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/ALBERTVILLE G.ILE 3 | AT | 0 | Reduction because ot disconnection of line 912 and 261
20231012 | 0330 | October | 7529 | 6939 | 2600 | 0 | -2525 | -2525 | -1947 | Critical Branch | Critical Branch | 590 | 0 | FR | 2600 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/ALBERTVILLE G.ILE 3 | AT | 0 | Reduction because ot disconnection of line 912 and 261
20231012 | 0430 | October | 7529 | 6939 | 2600 | 0 | -2525 | -2525 | -1947 | Critical Branch | Critical Branch | 590 | 0 | FR | 2600 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/ALBERTVILLE G.ILE 3 | AT | 0 | Reduction because ot disconnection of line 912 and 261
20231012 | 0530 | October | 7529 | 6939 | 2600 | 0 | -2525 | -2525 | -1947 | Critical Branch | Critical Branch | 590 | 0 | FR | 2600 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/ALBERTVILLE G.ILE 3 | AT | 0 | Reduction because ot disconnection of line 912 and 261
20231012 | 0630 | October | 7529 | 6939 | 2600 | 0 | -2525 | -2525 | -1947 | Critical Branch | Critical Branch | 590 | 0 | FR | 2600 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/ALBERTVILLE G.ILE 3 | AT | 0 | Reduction because ot disconnection of line 912 and 261
20231012 | 0730 | October | 7538 | 7139 | 2600 | 0 | -2885 | -2885 | -2411 | Critical Branch | Critical Branch | 399 | 0 | FR | 2600 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/ALBERTVILLE G.ILE 3 | AT | 0 | Reduction because ot disconnection of line 912 and 261
20231012 | 0830 | October | 7538 | 7139 | 2600 | 0 | -2885 | -2885 | -2411 | Critical Branch | Critical Branch | 399 | 0 | FR | 2600 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/ALBERTVILLE G.ILE 3 | AT | 0 | Reduction because ot disconnection of line 912 and 261
20231012 | 0930 | October | 7871 | 7330 | 2600 | 0 | -2738 | -2738 | -2086 | Critical Branch | Critical Branch | 541 | 0 | FR | 2600 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/ALBERTVILLE G.ILE 3 | AT | 0 | Reduction because ot disconnection of line 912 and 261
20231012 | 1030 | October | 7871 | 7330 | 2600 | 0 | -2738 | -2738 | -2086 | Critical Branch | Critical Branch | 541 | 0 | FR | 2600 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/ALBERTVILLE G.ILE 3 | AT | 0 | Reduction because ot disconnection of line 912 and 261
20231012 | 1130 | October | 7871 | 7330 | 2600 | 0 | -2738 | -2738 | -2086 | Critical Branch | Critical Branch | 541 | 0 | FR | 2600 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/ALBERTVILLE G.ILE 3 | AT | 0 | Reduction because ot disconnection of line 912 and 261
20231012 | 1230 | October | 8235 | 7539 | 2600 | 0 | -2834 | -2834 | -1987 | Critical Branch | Critical Branch | 696 | 0 | FR | 2600 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/ALBERTVILLE G.ILE 3 | AT | 0 | Reduction because ot disconnection of line 912 and 261
20231012 | 1330 | October | 8235 | 7539 | 2600 | 0 | -2834 | -2834 | -1987 | Critical Branch | Critical Branch | 696 | 0 | FR | 2600 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/ALBERTVILLE G.ILE 3 | AT | 0 | Reduction because ot disconnection of line 912 and 261
20231012 | 1430 | October | 8235 | 7539 | 2600 | 0 | -2834 | -2834 | -1987 | Critical Branch | Critical Branch | 696 | 0 | FR | 2600 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/ALBERTVILLE G.ILE 3 | AT | 0 | Reduction because ot disconnection of line 912 and 261
20231012 | 1530 | October | 8327 | 6884 | 2600 | 0 | -2843 | -2843 | -1340 | Critical Branch | Validation phase | 1443 | 0 | FR | 2600 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/ALBERTVILLE G.ILE 3 | AT | 0 | Reduction because ot disconnection of line 912 and 261 | CH | 6903 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231012 | 1630 | October | 8327 | 6884 | 2600 | 0 | -2843 | -2843 | -1340 | Critical Branch | Validation phase | 1443 | 0 | FR | 2600 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/ALBERTVILLE G.ILE 3 | AT | 0 | Reduction because ot disconnection of line 912 and 261 | CH | 6903 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231012 | 1730 | October | 9227 | 7734 | 2600 | 0 | -3608 | -3608 | -2042 | Critical Branch | Validation phase | 1493 | 0 | FR | 2600 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/ALBERTVILLE G.ILE 3 | AT | 0 | Reduction because ot disconnection of line 912 and 261 | CH | 7803 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231012 | 1830 | October | 7890 | 7110 | 2522 | 0 | -2993 | -2993 | -2214 | Critical Branch | Validation phase | 780 | 0 | CH | 6920 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231012 | 1930 | October | 7890 | 7110 | 2522 | 0 | -2993 | -2993 | -2214 | Critical Branch | Validation phase | 780 | 0 | CH | 6920 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231012 | 2030 | October | 7890 | 7110 | 2522 | 0 | -2993 | -2993 | -2214 | Critical Branch | Validation phase | 780 | 0 | CH | 6920 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231012 | 2130 | October | 8469 | 7354 | 2600 | 0 | -3183 | -3183 | -2069 | Critical Branch | Validation phase | 1115 | 0 | FR | 2600 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/ALBERTVILLE G.ILE 3 | AT | 0 | Reduction because ot disconnection of line 912 and 261 | CH | 7188 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231012 | 2230 | October | 8469 | 7354 | 2600 | 0 | -3183 | -3183 | -2069 | Critical Branch | Validation phase | 1115 | 0 | FR | 2600 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/ALBERTVILLE G.ILE 3 | AT | 0 | Reduction because ot disconnection of line 912 and 261 | CH | 7188 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231012 | 2330 | October | 7674 | 6583 | 2443 | 0 | -2377 | -2377 | -1286 | Critical Branch | Validation phase | 1091 | 0 | CH | 6393 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231013 | 0030 | October | 7770 | 6672 | 2600 | 0 | -1457 | -1457 | -382 | Critical Branch | Validation phase | 1098 | 0 | FR | 2600 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/ALBERTVILLE-G.ILE 3 | AT | 0 | Reduction because NTC over thermal limit on border | CH | 6849 | Missing CNEC in CC: CNE: 380kV Gorlago - Robbia , C: 380KV SILS-SOAZZA
20231013 | 0130 | October | 7770 | 6672 | 2600 | 0 | -1457 | -1457 | -382 | Critical Branch | Validation phase | 1098 | 0 | FR | 2600 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/ALBERTVILLE-G.ILE 3 | AT | 0 | Reduction because NTC over thermal limit on border | CH | 6849 | Missing CNEC in CC: CNE: 380kV Gorlago - Robbia , C: 380KV SILS-SOAZZA
20231013 | 0230 | October | 7770 | 6672 | 2600 | 0 | -1457 | -1457 | -382 | Critical Branch | Validation phase | 1098 | 0 | FR | 2600 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/ALBERTVILLE-G.ILE 3 | AT | 0 | Reduction because NTC over thermal limit on border | CH | 6849 | Missing CNEC in CC: CNE: 380kV Gorlago - Robbia , C: 380KV SILS-SOAZZA
20231013 | 0330 | October | 7773 | 6778 | 2600 | 0 | -1494 | -1494 | -502 | Critical Branch | Validation phase | 995 | 0 | FR | 2600 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/ALBERTVILLE-G.ILE 3 | AT | 0 | Reduction because NTC over thermal limit on border | CH | 7043 | Expected overloading on the following CNEC: CNE: 380kV Gorlago - Robbia , C: N-1 SOAZZA-BULCIAGO
20231013 | 0430 | October | 7773 | 6778 | 2600 | 0 | -1494 | -1494 | -502 | Critical Branch | Validation phase | 995 | 0 | FR | 2600 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/ALBERTVILLE-G.ILE 3 | AT | 0 | Reduction because NTC over thermal limit on border | CH | 7043 | Expected overloading on the following CNEC: CNE: 380kV Gorlago - Robbia , C: N-1 SOAZZA-BULCIAGO
20231013 | 0530 | October | 7773 | 6778 | 2600 | 0 | -1494 | -1494 | -502 | Critical Branch | Validation phase | 995 | 0 | FR | 2600 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/ALBERTVILLE-G.ILE 3 | AT | 0 | Reduction because NTC over thermal limit on border | CH | 7043 | Expected overloading on the following CNEC: CNE: 380kV Gorlago - Robbia , C: N-1 SOAZZA-BULCIAGO
20231013 | 0630 | October | 7773 | 6778 | 2600 | 0 | -1494 | -1494 | -502 | Critical Branch | Validation phase | 995 | 0 | FR | 2600 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/ALBERTVILLE-G.ILE 3 | AT | 0 | Reduction because NTC over thermal limit on border | CH | 7043 | Expected overloading on the following CNEC: CNE: 380kV Gorlago - Robbia , C: N-1 SOAZZA-BULCIAGO
20231013 | 0730 | October | 7793 | 7055 | 2600 | 0 | -1172 | -1172 | -454 | Critical Branch | Validation phase | 738 | 0 | FR | 2600 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/ALBERTVILLE-G.ILE 3 | AT | 0 | Reduction because NTC over thermal limit on border | CH | 7201 | Expected overloading on the following CNEC: CNE: 380kV Gorlago - Robbia , C: N-1 SOAZZA-BULCIAGO
20231013 | 0830 | October | 7793 | 7055 | 2600 | 0 | -1172 | -1172 | -454 | Critical Branch | Validation phase | 738 | 0 | FR | 2600 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/ALBERTVILLE-G.ILE 3 | AT | 0 | Reduction because NTC over thermal limit on border | CH | 7201 | Expected overloading on the following CNEC: CNE: 380kV Gorlago - Robbia , C: N-1 SOAZZA-BULCIAGO
20231013 | 0930 | October | 6960 | 6808 | 2600 | 0 | -4421 | -4421 | -4276 | TTC Selection - LTTC | TTC Selection - LTTC | 152 | 0 | FR | 2600 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/ALBERTVILLE-G.ILE 3 | AT | 0 | Reduction because NTC over thermal limit on border
20231013 | 1030 | October | 6960 | 6808 | 2600 | 0 | -4421 | -4421 | -4276 | TTC Selection - LTTC | TTC Selection - LTTC | 152 | 0 | FR | 2600 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/ALBERTVILLE-G.ILE 3 | AT | 0 | Reduction because NTC over thermal limit on border
20231013 | 1130 | October | 6960 | 6808 | 2600 | 0 | -4421 | -4421 | -4276 | TTC Selection - LTTC | TTC Selection - LTTC | 152 | 0 | FR | 2600 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/ALBERTVILLE-G.ILE 3 | AT | 0 | Reduction because NTC over thermal limit on border
20231013 | 1230 | October | 6960 | 6808 | 2600 | 0 | -3755 | -3755 | -3615 | TTC Selection - LTTC | TTC Selection - LTTC | 152 | 0 | FR | 2600 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/ALBERTVILLE-G.ILE 3 | AT | 0 | Reduction because NTC over thermal limit on border
20231013 | 1330 | October | 6960 | 6808 | 2600 | 0 | -3755 | -3755 | -3615 | TTC Selection - LTTC | TTC Selection - LTTC | 152 | 0 | FR | 2600 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/ALBERTVILLE-G.ILE 3 | AT | 0 | Reduction because NTC over thermal limit on border
20231013 | 1430 | October | 6960 | 6808 | 2600 | 0 | -3755 | -3755 | -3615 | TTC Selection - LTTC | TTC Selection - LTTC | 152 | 0 | FR | 2600 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/ALBERTVILLE-G.ILE 3 | AT | 0 | Reduction because NTC over thermal limit on border
20231013 | 1530 | October | 8233 | 6008 | 2347 | 0 | -4063 | -4063 | -1838 | Critical Branch | Validation phase | 2225 | 0 | CH | 5818 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231013 | 1630 | October | 8233 | 6008 | 2347 | 0 | -4063 | -4063 | -1838 | Critical Branch | Validation phase | 2225 | 0 | CH | 5818 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231013 | 1730 | October | 9133 | 6908 | 2445 | 0 | -4993 | -4993 | -2768 | Critical Branch | Validation phase | 2225 | 0 | CH | 6718 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231013 | 1830 | October | 8934 | 8158 | 2600 | 0 | -2887 | -2887 | -2170 | Critical Branch | Validation phase | 776 | 0 | FR | 2600 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/ALBERTVILLE-G.ILE 3 | AT | 0 | Reduction because NTC over thermal limit on border | CH | 8489 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Pradella-Robbia + Filisur-Robbia
20231013 | 1930 | October | 8934 | 8158 | 2600 | 0 | -2887 | -2887 | -2170 | Critical Branch | Validation phase | 776 | 0 | FR | 2600 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/ALBERTVILLE-G.ILE 3 | AT | 0 | Reduction because NTC over thermal limit on border | CH | 8489 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Pradella-Robbia + Filisur-Robbia
20231013 | 2030 | October | 8934 | 8158 | 2600 | 0 | -2887 | -2887 | -2170 | Critical Branch | Validation phase | 776 | 0 | FR | 2600 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/ALBERTVILLE-G.ILE 3 | AT | 0 | Reduction because NTC over thermal limit on border | CH | 8489 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Pradella-Robbia + Filisur-Robbia
20231013 | 2130 | October | 8691 | 8166 | 2600 | 0 | -2549 | -2549 | -2055 | Critical Branch | Critical Branch | 525 | 0 | FR | 2600 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/ALBERTVILLE-G.ILE 3 | AT | 0 | Reduction because NTC over thermal limit on border
20231013 | 2230 | October | 8691 | 8166 | 2600 | 0 | -2549 | -2549 | -2055 | Critical Branch | Critical Branch | 525 | 0 | FR | 2600 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/ALBERTVILLE-G.ILE 3 | AT | 0 | Reduction because NTC over thermal limit on border
20231013 | 2330 | October | 7896 | 7526 | 2600 | 0 | -1745 | -1745 | -1399 | Critical Branch | Critical Branch | 370 | 0 | FR | 2600 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/ALBERTVILLE-G.ILE 3 | AT | 0 | Reduction because NTC over thermal limit on border
20231014 | 0030 | October | 8420 | 7739 | 2600 | 0 | -3217 | -3217 | -2581 | Critical Branch | Validation phase | 681 | 0 | FR | 2600 | Bilateral - Problème Coordination TERNA |  |  |  | CH | 8061 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza , C: N-2 Pradella-Robbia + Filisur-Robbia
20231014 | 0130 | October | 8420 | 7739 | 2600 | 0 | -3217 | -3217 | -2581 | Critical Branch | Validation phase | 681 | 0 | FR | 2600 | Bilateral - Problème Coordination TERNA |  |  |  | CH | 8061 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza , C: N-2 Pradella-Robbia + Filisur-Robbia
20231014 | 0230 | October | 8420 | 7739 | 2600 | 0 | -3217 | -3217 | -2581 | Critical Branch | Validation phase | 681 | 0 | FR | 2600 | Bilateral - Problème Coordination TERNA |  |  |  | CH | 8061 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza , C: N-2 Pradella-Robbia + Filisur-Robbia
20231014 | 0330 | October | 8684 | 7841 | 2600 | 0 | -1561 | -1561 | -784 | Critical Branch | Validation phase | 843 | 0 | FR | 2600 | Bilateral - Problème Coordination TERNA |  |  |  | CH | 8232 | Expected overloading on the following CNEC: CNE: 380kV Filisur - Sils , C: N-1 PRADELLA-ROBBIA
20231014 | 0430 | October | 8684 | 7841 | 2600 | 0 | -1561 | -1561 | -784 | Critical Branch | Validation phase | 843 | 0 | FR | 2600 | Bilateral - Problème Coordination TERNA |  |  |  | CH | 8232 | Expected overloading on the following CNEC: CNE: 380kV Filisur - Sils , C: N-1 PRADELLA-ROBBIA
20231014 | 0530 | October | 8684 | 7841 | 2600 | 0 | -1561 | -1561 | -784 | Critical Branch | Validation phase | 843 | 0 | FR | 2600 | Bilateral - Problème Coordination TERNA |  |  |  | CH | 8232 | Expected overloading on the following CNEC: CNE: 380kV Filisur - Sils , C: N-1 PRADELLA-ROBBIA
20231014 | 0630 | October | 8684 | 7841 | 2600 | 0 | -1561 | -1561 | -784 | Critical Branch | Validation phase | 843 | 0 | FR | 2600 | Bilateral - Problème Coordination TERNA |  |  |  | CH | 8232 | Expected overloading on the following CNEC: CNE: 380kV Filisur - Sils , C: N-1 PRADELLA-ROBBIA
20231014 | 0730 | October | 8847 | 8091 | 2600 | 0 | -1947 | -1947 | -1256 | Critical Branch | Validation phase | 756 | 0 | FR | 2600 | Bilateral - Problème Coordination TERNA |  |  |  | CH | 8380 | Expected overloading on the following CNEC: CNE: 380kV Filisur - Sils , C: N-1 PRADELLA-ROBBIA
20231014 | 0830 | October | 8847 | 8091 | 2600 | 0 | -1947 | -1947 | -1256 | Critical Branch | Validation phase | 756 | 0 | FR | 2600 | Bilateral - Problème Coordination TERNA |  |  |  | CH | 8380 | Expected overloading on the following CNEC: CNE: 380kV Filisur - Sils , C: N-1 PRADELLA-ROBBIA
20231014 | 0930 | October | 7860 | 7652 | 2600 | 0 | -4265 | -4265 | -4070 | TTC Selection - LTTC | TTC Selection - LTTC | 208 | 0 | FR | 2600 | Bilateral - Problème Coordination TERNA
20231014 | 1030 | October | 7860 | 7652 | 2600 | 0 | -4265 | -4265 | -4070 | TTC Selection - LTTC | TTC Selection - LTTC | 208 | 0 | FR | 2600 | Bilateral - Problème Coordination TERNA
20231014 | 1130 | October | 7860 | 7652 | 2600 | 0 | -4265 | -4265 | -4070 | TTC Selection - LTTC | TTC Selection - LTTC | 208 | 0 | FR | 2600 | Bilateral - Problème Coordination TERNA
20231014 | 1230 | October | 7860 | 7546 | 2600 | 0 | -2801 | -2801 | -2497 | TTC Selection - LTTC | Validation phase | 314 | 0 | FR | 2600 | Bilateral - Problème Coordination TERNA |  |  |  | CH | 7499 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza , C: N-2 Pradella-Robbia + Filisur-Robbia
20231014 | 1330 | October | 7860 | 7546 | 2600 | 0 | -2801 | -2801 | -2497 | TTC Selection - LTTC | Validation phase | 314 | 0 | FR | 2600 | Bilateral - Problème Coordination TERNA |  |  |  | CH | 7499 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza , C: N-2 Pradella-Robbia + Filisur-Robbia
20231014 | 1430 | October | 7860 | 7546 | 2600 | 0 | -2801 | -2801 | -2497 | TTC Selection - LTTC | Validation phase | 314 | 0 | FR | 2600 | Bilateral - Problème Coordination TERNA |  |  |  | CH | 7499 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza , C: N-2 Pradella-Robbia + Filisur-Robbia
20231014 | 1530 | October | 9067 | 7625 | 2600 | 0 | -2889 | -2889 | -1463 | Critical Branch | Validation phase | 1442 | 0 | FR | 2600 | Bilateral - Problème Coordination TERNA |  |  |  | CH | 7626 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231014 | 1630 | October | 9067 | 7625 | 2600 | 0 | -2889 | -2889 | -1463 | Critical Branch | Validation phase | 1442 | 0 | FR | 2600 | Bilateral - Problème Coordination TERNA |  |  |  | CH | 7626 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231014 | 1730 | October | 9067 | 7625 | 2600 | 0 | -2889 | -2889 | -1463 | Critical Branch | Validation phase | 1442 | 0 | FR | 2600 | Bilateral - Problème Coordination TERNA |  |  |  | CH | 7626 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231014 | 1830 | October | 9083 | 8103 | 2600 | 0 | -4775 | -4775 | -3801 | Critical Branch | Validation phase | 980 | 0 | FR | 2600 | Bilateral - Problème Coordination TERNA |  |  |  | IT | 8400 | PLL-SRR su Ponte-Acqua 130%
20231014 | 1930 | October | 9083 | 8103 | 2600 | 0 | -4775 | -4775 | -3801 | Critical Branch | Validation phase | 980 | 0 | FR | 2600 | Bilateral - Problème Coordination TERNA |  |  |  | IT | 8400 | PLL-SRR su Ponte-Acqua 130%
20231014 | 2030 | October | 9083 | 8103 | 2600 | 0 | -4775 | -4775 | -3801 | Critical Branch | Validation phase | 980 | 0 | FR | 2600 | Bilateral - Problème Coordination TERNA |  |  |  | IT | 8400 | PLL-SRR su Ponte-Acqua 130%
20231014 | 2130 | October | 8858 | 7800 | 2600 | 0 | -3383 | -3383 | -2351 | Critical Branch | Validation phase | 1058 | 0 | FR | 2600 | Bilateral - Problème Coordination TERNA |  |  |  | CH | 7910 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231014 | 2230 | October | 8858 | 7800 | 2600 | 0 | -3383 | -3383 | -2351 | Critical Branch | Validation phase | 1058 | 0 | FR | 2600 | Bilateral - Problème Coordination TERNA |  |  |  | CH | 7910 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231014 | 2330 | October | 8063 | 7173 | 2600 | 0 | -2571 | -2571 | -1693 | Critical Branch | Validation phase | 890 | 0 | FR | 2600 | Bilateral - Problème Coordination TERNA |  |  |  | CH | 7115 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231015 | 0030 | October | 7670 | 7391 | 2600 | 0 | -2798 | -2798 | -2539 | Critical Branch | Critical Branch | 279 | 0 | FR | 2600 | Bilateral - Problème Coordination TERNA | AT | 0 | Reduction because NTC over thermal limit on border
20231015 | 0130 | October | 7670 | 7391 | 2600 | 0 | -2798 | -2798 | -2539 | Critical Branch | Critical Branch | 279 | 0 | FR | 2600 | Bilateral - Problème Coordination TERNA | AT | 0 | Reduction because NTC over thermal limit on border
20231015 | 0230 | October | 7670 | 7391 | 2600 | 0 | -2798 | -2798 | -2539 | Critical Branch | Critical Branch | 279 | 0 | FR | 2600 | Bilateral - Problème Coordination TERNA | AT | 0 | Reduction because NTC over thermal limit on border
20231015 | 0330 | October | 8168 | 7689 | 2600 | 0 | -1955 | -1955 | -1514 | Critical Branch | Critical Branch | 479 | 0 | FR | 2600 | Bilateral - Problème Coordination TERNA | AT | 0 | Reduction because NTC over thermal limit on border
20231015 | 0430 | October | 8168 | 7689 | 2600 | 0 | -1955 | -1955 | -1514 | Critical Branch | Critical Branch | 479 | 0 | FR | 2600 | Bilateral - Problème Coordination TERNA | AT | 0 | Reduction because NTC over thermal limit on border
20231015 | 0530 | October | 8168 | 7689 | 2600 | 0 | -1955 | -1955 | -1514 | Critical Branch | Critical Branch | 479 | 0 | FR | 2600 | Bilateral - Problème Coordination TERNA | AT | 0 | Reduction because NTC over thermal limit on border
20231015 | 0630 | October | 8168 | 7689 | 2600 | 0 | -1955 | -1955 | -1514 | Critical Branch | Critical Branch | 479 | 0 | FR | 2600 | Bilateral - Problème Coordination TERNA | AT | 0 | Reduction because NTC over thermal limit on border
20231015 | 0930 | October | 9204 | 8124 | 2600 | 0 | -3455 | -3455 | -2469 | Critical Branch | Validation phase | 1080 | 0 | FR | 2600 | Bilateral - Problème Coordination TERNA | AT | 0 | Reduction because NTC over thermal limit on border | CH | 8705 | Expected overloading on the following CNEC: CNE: 380kV Fiorano - Robbia , C: 380KV GORLAGO-ROBBIA
20231015 | 1030 | October | 9204 | 8124 | 2600 | 0 | -3455 | -3455 | -2469 | Critical Branch | Validation phase | 1080 | 0 | FR | 2600 | Bilateral - Problème Coordination TERNA | AT | 0 | Reduction because NTC over thermal limit on border | CH | 8705 | Expected overloading on the following CNEC: CNE: 380kV Fiorano - Robbia , C: 380KV GORLAGO-ROBBIA
20231015 | 1130 | October | 9204 | 8124 | 2600 | 0 | -3455 | -3455 | -2469 | Critical Branch | Validation phase | 1080 | 0 | FR | 2600 | Bilateral - Problème Coordination TERNA | AT | 0 | Reduction because NTC over thermal limit on border | CH | 8705 | Expected overloading on the following CNEC: CNE: 380kV Fiorano - Robbia , C: 380KV GORLAGO-ROBBIA
20231015 | 1230 | October | 8690 | 8001 | 2600 | 0 | -1456 | -1456 | -815 | Critical Branch | Critical Branch | 689 | 0 | FR | 2600 | Bilateral - Problème Coordination TERNA | AT | 0 | Reduction because NTC over thermal limit on border
20231015 | 1330 | October | 8690 | 8001 | 2600 | 0 | -1456 | -1456 | -815 | Critical Branch | Critical Branch | 689 | 0 | FR | 2600 | Bilateral - Problème Coordination TERNA | AT | 0 | Reduction because NTC over thermal limit on border
20231015 | 1430 | October | 8690 | 8001 | 2600 | 0 | -1456 | -1456 | -815 | Critical Branch | Critical Branch | 689 | 0 | FR | 2600 | Bilateral - Problème Coordination TERNA | AT | 0 | Reduction because NTC over thermal limit on border
20231015 | 1530 | October | 7951 | 7559 | 2600 | 0 | -6970 | -6970 | -6567 | Critical Branch | Critical Branch | 392 | 0 | FR | 2600 | Bilateral - Problème Coordination TERNA | AT | 0 | Reduction because NTC over thermal limit on border
20231015 | 1630 | October | 7951 | 7559 | 2600 | 0 | -6970 | -6970 | -6567 | Critical Branch | Critical Branch | 392 | 0 | FR | 2600 | Bilateral - Problème Coordination TERNA | AT | 0 | Reduction because NTC over thermal limit on border
20231015 | 1730 | October | 7951 | 7559 | 2600 | 0 | -6970 | -6970 | -6567 | Critical Branch | Critical Branch | 392 | 0 | FR | 2600 | Bilateral - Problème Coordination TERNA | AT | 0 | Reduction because NTC over thermal limit on border
20231015 | 1830 | October | 9074 | 8133 | 2600 | 0 | -1702 | -1702 | -864 | Critical Branch | Validation phase | 941 | 0 | FR | 2600 | Bilateral - Problème Coordination TERNA | AT | 0 | Reduction because NTC over thermal limit on border | CH | 8720 | Expected overloading on the following CNEC: CNE: 380kV Fiorano - Robbia , C: 380KV GORLAGO-ROBBIA
20231015 | 1930 | October | 9074 | 8133 | 2600 | 0 | -1702 | -1702 | -864 | Critical Branch | Validation phase | 941 | 0 | FR | 2600 | Bilateral - Problème Coordination TERNA | AT | 0 | Reduction because NTC over thermal limit on border | CH | 8720 | Expected overloading on the following CNEC: CNE: 380kV Fiorano - Robbia , C: 380KV GORLAGO-ROBBIA
20231015 | 2030 | October | 9074 | 8133 | 2600 | 0 | -1702 | -1702 | -864 | Critical Branch | Validation phase | 941 | 0 | FR | 2600 | Bilateral - Problème Coordination TERNA | AT | 0 | Reduction because NTC over thermal limit on border | CH | 8720 | Expected overloading on the following CNEC: CNE: 380kV Fiorano - Robbia , C: 380KV GORLAGO-ROBBIA
20231015 | 2130 | October | 9863 | 8134 | 2600 | 0 | -3081 | -3081 | -1412 | Critical Branch | Validation phase | 1729 | 0 | FR | 2600 | Bilateral - Problème Coordination TERNA | AT | 0 | Reduction because NTC over thermal limit on border | CH | 8722 | Expected overloading on the following CNEC: CNE: 380kV Fiorano - Robbia , C: 380KV GORLAGO-ROBBIA
20231015 | 2230 | October | 9863 | 8134 | 2600 | 0 | -3081 | -3081 | -1412 | Critical Branch | Validation phase | 1729 | 0 | FR | 2600 | Bilateral - Problème Coordination TERNA | AT | 0 | Reduction because NTC over thermal limit on border | CH | 8722 | Expected overloading on the following CNEC: CNE: 380kV Fiorano - Robbia , C: 380KV GORLAGO-ROBBIA
20231015 | 2330 | October | 9863 | 8134 | 2600 | 0 | -3081 | -3081 | -1412 | Critical Branch | Validation phase | 1729 | 0 | FR | 2600 | Bilateral - Problème Coordination TERNA | AT | 0 | Reduction because NTC over thermal limit on border | CH | 8722 | Expected overloading on the following CNEC: CNE: 380kV Fiorano - Robbia , C: 380KV GORLAGO-ROBBIA
20231016 | 0030 | October | 9271 | 7691 | 2600 | 0 | -3787 | -3787 | -2214 | Critical Branch | Validation phase | 1580 | 0 | FR | 2600 | Bilateral - Red Flag RTE |  |  |  | IT | 7981 | Expected overloading on the following CNEC: CNE: 380kV Fiorano - Robbia , C: 380KV GORLAGO-ROBBIA
20231016 | 0130 | October | 9271 | 7691 | 2600 | 0 | -3787 | -3787 | -2214 | Critical Branch | Validation phase | 1580 | 0 | FR | 2600 | Bilateral - Red Flag RTE |  |  |  | IT | 7981 | Expected overloading on the following CNEC: CNE: 380kV Fiorano - Robbia , C: 380KV GORLAGO-ROBBIA
20231016 | 0230 | October | 9271 | 7691 | 2600 | 0 | -3787 | -3787 | -2214 | Critical Branch | Validation phase | 1580 | 0 | FR | 2600 | Bilateral - Red Flag RTE |  |  |  | IT | 7981 | Expected overloading on the following CNEC: CNE: 380kV Fiorano - Robbia , C: 380KV GORLAGO-ROBBIA
20231016 | 0330 | October | 7322 | 7183 | 2600 | 0 | -2709 | -2709 | -2500 | Critical Branch | Critical Branch | 139 | 0 | FR | 2600 | Bilateral - Red Flag RTE
20231016 | 0430 | October | 7322 | 7183 | 2600 | 0 | -2709 | -2709 | -2500 | Critical Branch | Critical Branch | 139 | 0 | FR | 2600 | Bilateral - Red Flag RTE
20231016 | 0530 | October | 7322 | 7183 | 2600 | 0 | -2709 | -2709 | -2500 | Critical Branch | Critical Branch | 139 | 0 | FR | 2600 | Bilateral - Red Flag RTE
20231016 | 0630 | October | 7258 | 7122 | 2600 | 0 | -2664 | -2664 | -2460 | Critical Branch | Critical Branch | 136 | 0 | FR | 2600 | Bilateral - Red Flag RTE
20231016 | 0730 | October | 7243 | 6774 | 2107 | 0 | -4427 | -4427 | -3958 | Critical Branch | Validation phase | 469 | 0 | CH | 6584 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231016 | 0830 | October | 7043 | 6574 | 2112 | 0 | -4225 | -4225 | -3756 | Critical Branch | Validation phase | 469 | 0 | CH | 6384 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231016 | 1230 | October | 6457 | 6389 | 2047 | 0 | -2747 | -2747 | -2679 | Critical Branch | Validation phase | 68 | 0 | CH | 6199 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231016 | 1330 | October | 6457 | 6389 | 2047 | 0 | -2747 | -2747 | -2679 | Critical Branch | Validation phase | 68 | 0 | CH | 6199 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231016 | 1430 | October | 6457 | 6389 | 2047 | 0 | -2747 | -2747 | -2679 | Critical Branch | Validation phase | 68 | 0 | CH | 6199 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231016 | 1530 | October | 6571 | 6432 | 2062 | 0 | -3213 | -3213 | -3074 | Critical Branch | Validation phase | 139 | 0 | CH | 6242 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231016 | 1630 | October | 6571 | 6432 | 2062 | 0 | -3213 | -3213 | -3074 | Critical Branch | Validation phase | 139 | 0 | CH | 6242 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231016 | 1730 | October | 6571 | 6432 | 2062 | 0 | -3213 | -3213 | -3074 | Critical Branch | Validation phase | 139 | 0 | CH | 6242 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231016 | 2130 | October | 6560 | 6451 | 2069 | 0 | 273 | 273 | 109 | Minimum Margin | Validation phase | 109 | 109 | CH | 6261 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231016 | 2230 | October | 6560 | 6451 | 2069 | 0 | 273 | 273 | 109 | Minimum Margin | Validation phase | 109 | 109 | CH | 6261 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231017 | 2130 | October | 6734 | 6190 | 1978 | 0 | -3472 | -3472 | -2928 | Critical Branch | Validation phase | 544 | 0 | CH | 6000 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231017 | 2230 | October | 6734 | 6190 | 1978 | 0 | -3472 | -3472 | -2928 | Critical Branch | Validation phase | 544 | 0 | CH | 6000 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231017 | 2330 | October | 6139 | 5595 | 1831 | 0 | -2886 | -2886 | -2342 | Critical Branch | Validation phase | 544 | 0 | CH | 5405 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231018 | 0030 | October | 6751 | 6144 | 2028 | 0 | -897 | -897 | -290 | Critical Branch | Validation phase | 607 | 0 | CH | 5954 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231018 | 0130 | October | 6751 | 6144 | 2028 | 0 | -897 | -897 | -290 | Critical Branch | Validation phase | 607 | 0 | CH | 5954 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231018 | 0230 | October | 6751 | 6144 | 2028 | 0 | -897 | -897 | -290 | Critical Branch | Validation phase | 607 | 0 | CH | 5954 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231018 | 0330 | October | 5849 | 5772 | 1894 | 0 | -2416 | -2416 | -2339 | Critical Branch | Validation phase | 77 | 0 | CH | 5582 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231018 | 0430 | October | 5849 | 5772 | 1894 | 0 | -2416 | -2416 | -2339 | Critical Branch | Validation phase | 77 | 0 | CH | 5582 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231018 | 0530 | October | 5849 | 5772 | 1894 | 0 | -2416 | -2416 | -2339 | Critical Branch | Validation phase | 77 | 0 | CH | 5582 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231018 | 0630 | October | 5849 | 5772 | 1894 | 0 | -2416 | -2416 | -2339 | Critical Branch | Validation phase | 77 | 0 | CH | 5582 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231018 | 0730 | October | 6745 | 6503 | 2087 | 0 | -1316 | -1316 | -1074 | Critical Branch | Validation phase | 242 | 0 | CH | 6313 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Pradella-Robbia + Filisur-Robbia
20231018 | 0830 | October | 6745 | 6503 | 2087 | 0 | -1316 | -1316 | -1074 | Critical Branch | Validation phase | 242 | 0 | CH | 6313 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Pradella-Robbia + Filisur-Robbia
20231018 | 1530 | October | 6852 | 5419 | 1710 | 0 | -1076 | -1076 | 357 | Critical Branch | Validation phase | 1433 | 357 | CH | 5229 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231018 | 1630 | October | 6852 | 5419 | 1710 | 0 | -1076 | -1076 | 357 | Critical Branch | Validation phase | 1433 | 357 | CH | 5229 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231018 | 1730 | October | 6852 | 5419 | 1710 | 0 | -1076 | -1076 | 357 | Critical Branch | Validation phase | 1433 | 357 | CH | 5229 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231018 | 2130 | October | 7111 | 5148 | 1616 | 0 | -1934 | -1934 | 29 | Critical Branch | Validation phase | 1963 | 29 | CH | 4958 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231018 | 2230 | October | 7111 | 5148 | 1616 | 0 | -1934 | -1934 | 29 | Critical Branch | Validation phase | 1963 | 29 | CH | 4958 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231018 | 2330 | October | 6516 | 4553 | 1456 | 0 | -1339 | -1339 | 624 | Critical Branch | Validation phase | 1963 | 624 | CH | 4363 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231019 | 0630 | October | 6482 | 5916 | 1946 | 0 | -2715 | -2715 | -2149 | Critical Branch | Smoothing ramp | 566 | 0 | Smoothing
20231019 | 0730 | October | 6938 | 4416 | 1361 | 0 | -1462 | -1462 | 1060 | Critical Branch | Validation phase | 2522 | 1060 | CH | 4226 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231019 | 0830 | October | 6938 | 4416 | 1361 | 0 | -1462 | -1462 | 1060 | Critical Branch | Validation phase | 2522 | 1060 | CH | 4226 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231019 | 0930 | October | 6098 | 5916 | 1883 | 0 | -4503 | -4503 | -4321 | Critical Branch | Smoothing ramp | 182 | 0 | Smoothing
20231019 | 1830 | October | 7196 | 6398 | 2050 | 0 | -1437 | -1437 | -639 | Critical Branch | Validation phase | 798 | 0 | CH | 6208 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231019 | 1930 | October | 7196 | 5916 | 1883 | 0 | -1437 | -1437 | -157 | Critical Branch | Smoothing ramp | 1280 | 0 | Smoothing
20231019 | 2030 | October | 7196 | 4416 | 1361 | 0 | -1437 | -1437 | 1343 | Critical Branch | Smoothing ramp | 2780 | 1343 | Smoothing
20231019 | 2130 | October | 6842 | 2916 | 840 | 0 | -1193 | -1193 | 2733 | Critical Branch | Smoothing ramp | 3926 | 2733 | Smoothing
20231019 | 2230 | October | 6842 | 1416 | 318 | 0 | -1193 | -1193 | 4233 | Critical Branch | Smoothing ramp | 5426 | 4233 | Smoothing
20231019 | 2330 | October | 1058 | -84 | 0 | 0 | 5156 | 558 | 5156 | Minimum Margin | Minimum Margin | 1142 | 558 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231020 | 0030 | October | 5615 | 5177 | 1400 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 438 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE GRANDE ILE
20231020 | 0130 | October | 5615 | 5177 | 1400 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 438 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE GRANDE ILE
20231020 | 0230 | October | 5615 | 5177 | 1400 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 438 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE GRANDE ILE
20231020 | 0330 | October | 5615 | 5177 | 1400 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 438 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE GRANDE ILE
20231020 | 0430 | October | 5615 | 5177 | 1400 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 438 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE GRANDE ILE
20231020 | 0530 | October | 5615 | 5177 | 1400 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 438 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE GRANDE ILE
20231020 | 0630 | October | 5615 | 5177 | 1400 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 438 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE GRANDE ILE
20231020 | 0730 | October | 6210 | 5625 | 1400 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 585 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE GRANDE ILE
20231020 | 0830 | October | 6210 | 5625 | 1400 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 585 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE GRANDE ILE
20231020 | 0930 | October | 6210 | 5625 | 1400 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 585 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE GRANDE ILE
20231020 | 1030 | October | 6210 | 5625 | 1400 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 585 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE GRANDE ILE
20231020 | 1130 | October | 6210 | 5625 | 1400 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 585 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE GRANDE ILE
20231020 | 1230 | October | 6210 | 5625 | 1400 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 585 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE GRANDE ILE
20231020 | 1330 | October | 6210 | 5625 | 1400 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 585 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE GRANDE ILE
20231020 | 1430 | October | 6210 | 5625 | 1400 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 585 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE GRANDE ILE
20231020 | 1530 | October | 6210 | 5625 | 1400 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 585 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE GRANDE ILE
20231020 | 1630 | October | 6410 | 5825 | 1400 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 585 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE GRANDE ILE
20231020 | 1730 | October | 6410 | 5825 | 1400 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 585 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE GRANDE ILE
20231020 | 1830 | October | 6410 | 5825 | 1400 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 585 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE GRANDE ILE
20231020 | 1930 | October | 6410 | 5825 | 1400 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 585 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE GRANDE ILE
20231020 | 2030 | October | 6410 | 5825 | 1400 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 585 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE GRANDE ILE
20231020 | 2130 | October | 6410 | 5825 | 1400 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 585 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE GRANDE ILE
20231020 | 2230 | October | 6410 | 5825 | 1400 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 585 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE GRANDE ILE
20231020 | 2330 | October | 5815 | 5377 | 1400 | 0 |  |  |  | Scheduled TTC | Scheduled TTC | 438 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE GRANDE ILE
20231021 | 0030 | October | 7604 | 6080 | 1400 | 0 | -4063 | -4063 | -2605 | Critical Branch | Validation phase | 1524 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT |  |  |  | IT | 6700 | N-2 ABV-RON/N-2 ABV GRA on 220 kV FR-IT and CH-IT grid
20231021 | 0130 | October | 7604 | 6080 | 1400 | 0 | -4063 | -4063 | -2605 | Critical Branch | Validation phase | 1524 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT |  |  |  | IT | 6700 | N-2 ABV-RON/N-2 ABV GRA on 220 kV FR-IT and CH-IT grid
20231021 | 0230 | October | 7604 | 6080 | 1400 | 0 | -4063 | -4063 | -2605 | Critical Branch | Validation phase | 1524 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT |  |  |  | IT | 6700 | N-2 ABV-RON/N-2 ABV GRA on 220 kV FR-IT and CH-IT grid
20231021 | 0330 | October | 7088 | 5921 | 1400 | 0 | -3322 | -3322 | -2220 | Critical Branch | Validation phase | 1167 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT |  |  |  | CH | 6456 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza , C: N-2 Pradella-Robbia + Filisur-Robbia
20231021 | 0430 | October | 7088 | 5921 | 1400 | 0 | -3322 | -3322 | -2220 | Critical Branch | Validation phase | 1167 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT |  |  |  | CH | 6456 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza , C: N-2 Pradella-Robbia + Filisur-Robbia
20231021 | 0530 | October | 7088 | 5921 | 1400 | 0 | -3322 | -3322 | -2220 | Critical Branch | Validation phase | 1167 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT |  |  |  | CH | 6456 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza , C: N-2 Pradella-Robbia + Filisur-Robbia
20231021 | 0630 | October | 7088 | 5921 | 1400 | 0 | -3322 | -3322 | -2220 | Critical Branch | Validation phase | 1167 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT |  |  |  | CH | 6456 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza , C: N-2 Pradella-Robbia + Filisur-Robbia
20231021 | 0730 | October | 7220 | 5945 | 1400 | 0 | -1365 | -1365 | -211 | Critical Branch | Validation phase | 1275 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT |  |  |  | IT | 6400 | N-2 ABV-RON/N-2 ABV GRA on 220 kV FR-IT and CH-IT grid
20231021 | 0830 | October | 7220 | 5945 | 1400 | 0 | -1365 | -1365 | -211 | Critical Branch | Validation phase | 1275 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT |  |  |  | IT | 6400 | N-2 ABV-RON/N-2 ABV GRA on 220 kV FR-IT and CH-IT grid
20231021 | 0930 | October | 6288 | 5585 | 1400 | 0 | -1777 | -1777 | -1130 | Critical Branch | Validation phase | 703 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT |  |  |  | CH | 5858 | Missing CNEC in CC: CNE: 220kV Ponte - Y/Acqua , C: N-2 Pradella-Robbia + Filisur-Robbia
20231021 | 1030 | October | 6288 | 5585 | 1400 | 0 | -1777 | -1777 | -1130 | Critical Branch | Validation phase | 703 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT |  |  |  | CH | 5858 | Missing CNEC in CC: CNE: 220kV Ponte - Y/Acqua , C: N-2 Pradella-Robbia + Filisur-Robbia
20231021 | 1130 | October | 6288 | 5585 | 1400 | 0 | -1777 | -1777 | -1130 | Critical Branch | Validation phase | 703 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT |  |  |  | CH | 5858 | Missing CNEC in CC: CNE: 220kV Ponte - Y/Acqua , C: N-2 Pradella-Robbia + Filisur-Robbia
20231021 | 1230 | October | 5792 | 5415 | 1400 | 0 | -1381 | -1381 | -1052 | Critical Branch | Critical Branch | 377 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT
20231021 | 1330 | October | 5792 | 5415 | 1400 | 0 | -1381 | -1381 | -1052 | Critical Branch | Critical Branch | 377 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT
20231021 | 1430 | October | 5792 | 5415 | 1400 | 0 | -1381 | -1381 | -1052 | Critical Branch | Critical Branch | 377 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT
20231021 | 1530 | October | 6609 | 5948 | 1400 | 0 | -1828 | -1828 | -1217 | Critical Branch | Validation phase | 661 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT |  |  |  | CH | 6405 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231021 | 1630 | October | 6609 | 5948 | 1400 | 0 | -1828 | -1828 | -1217 | Critical Branch | Validation phase | 661 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT |  |  |  | CH | 6405 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231021 | 1730 | October | 6609 | 5948 | 1400 | 0 | -1828 | -1828 | -1217 | Critical Branch | Validation phase | 661 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT |  |  |  | CH | 6405 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231021 | 1830 | October | 6598 | 5828 | 1400 | 0 | -1278 | -1278 | -627 | Critical Branch | Validation phase | 770 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT |  |  |  | CH | 6225 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231021 | 1930 | October | 6598 | 5828 | 1400 | 0 | -1278 | -1278 | -627 | Critical Branch | Validation phase | 770 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT |  |  |  | CH | 6225 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231021 | 2030 | October | 6598 | 5828 | 1400 | 0 | -1278 | -1278 | -627 | Critical Branch | Validation phase | 770 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT |  |  |  | CH | 6225 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231021 | 2130 | October | 5590 | 5280 | 1400 | 0 | -1683 | -1683 | -1394 | Critical Branch | Critical Branch | 310 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT
20231021 | 2230 | October | 5590 | 5280 | 1400 | 0 | -1683 | -1683 | -1394 | Critical Branch | Critical Branch | 310 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT
20231021 | 2330 | October | 4995 | 4841 | 1400 | 0 | -1088 | -1088 | -945 | Critical Branch | Critical Branch | 154 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT
20231022 | 0030 | October | 6490 | 5722 | 1400 | 0 | -2843 | -2843 | -2070 | Critical Branch | Validation phase | 768 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT |  |  |  | CH | 6152 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231022 | 0130 | October | 6490 | 5722 | 1400 | 0 | -2843 | -2843 | -2070 | Critical Branch | Validation phase | 768 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT |  |  |  | CH | 6152 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231022 | 0230 | October | 6490 | 5722 | 1400 | 0 | -2843 | -2843 | -2070 | Critical Branch | Validation phase | 768 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT |  |  |  | CH | 6152 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231022 | 0330 | October | 5933 | 5454 | 1400 | 0 | -1488 | -1488 | -1076 | Critical Branch | Critical Branch | 479 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT
20231022 | 0430 | October | 5933 | 5454 | 1400 | 0 | -1488 | -1488 | -1076 | Critical Branch | Critical Branch | 479 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT
20231022 | 0530 | October | 5933 | 5454 | 1400 | 0 | -1488 | -1488 | -1076 | Critical Branch | Critical Branch | 479 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT
20231022 | 0630 | October | 5933 | 5454 | 1400 | 0 | -1488 | -1488 | -1076 | Critical Branch | Critical Branch | 479 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT
20231022 | 0730 | October | 6105 | 5567 | 1400 | 0 | -1769 | -1769 | -1274 | Critical Branch | Critical Branch | 538 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT
20231022 | 0830 | October | 6105 | 5567 | 1400 | 0 | -1769 | -1769 | -1274 | Critical Branch | Critical Branch | 538 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT
20231022 | 0930 | October | 6033 | 5520 | 1400 | 0 | -3262 | -3262 | -2779 | Critical Branch | Critical Branch | 513 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT
20231022 | 1030 | October | 6033 | 5520 | 1400 | 0 | -3262 | -3262 | -2779 | Critical Branch | Critical Branch | 513 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT
20231022 | 1130 | October | 6033 | 5520 | 1400 | 0 | -3262 | -3262 | -2779 | Critical Branch | Critical Branch | 513 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT
20231022 | 1230 | October | 5884 | 5422 | 1400 | 0 | -2745 | -2745 | -2323 | Critical Branch | Critical Branch | 462 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT
20231022 | 1330 | October | 5884 | 5422 | 1400 | 0 | -2745 | -2745 | -2323 | Critical Branch | Critical Branch | 462 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT
20231022 | 1430 | October | 5884 | 5422 | 1400 | 0 | -2745 | -2745 | -2323 | Critical Branch | Critical Branch | 462 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT
20231022 | 1530 | October | 6368 | 5683 | 1400 | 0 | -1311 | -1311 | -715 | Critical Branch | Validation phase | 685 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT |  |  |  | CH | 6093 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza , C: N-2 Pradella-Robbia + Filisur-Robbia
20231022 | 1630 | October | 6368 | 5683 | 1400 | 0 | -1311 | -1311 | -715 | Critical Branch | Validation phase | 685 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT |  |  |  | CH | 6093 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza , C: N-2 Pradella-Robbia + Filisur-Robbia
20231022 | 1730 | October | 6368 | 5683 | 1400 | 0 | -1311 | -1311 | -715 | Critical Branch | Validation phase | 685 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT |  |  |  | CH | 6093 | Expected overloading on the following CNEC: CNE: 380kV Sils - Soazza , C: N-2 Pradella-Robbia + Filisur-Robbia
20231022 | 1830 | October | 6196 | 5518 | 1400 | 0 | -1057 | -1057 | -485 | Critical Branch | Validation phase | 678 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT |  |  |  | CH | 5840 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Pradella-Robbia + Filisur-Robbia
20231022 | 1930 | October | 6196 | 5518 | 1400 | 0 | -1057 | -1057 | -485 | Critical Branch | Validation phase | 678 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT |  |  |  | CH | 5840 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Pradella-Robbia + Filisur-Robbia
20231022 | 2030 | October | 6196 | 5518 | 1400 | 0 | -1057 | -1057 | -485 | Critical Branch | Validation phase | 678 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT |  |  |  | CH | 5840 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Pradella-Robbia + Filisur-Robbia
20231023 | 0030 | October | 6544 | 5453 | 1400 | 0 | -3735 | -3735 | -2445 | Critical Branch | Critical Branch | 1091 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT
20231023 | 0130 | October | 6544 | 5453 | 1400 | 0 | -3735 | -3735 | -2445 | Critical Branch | Critical Branch | 1091 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT
20231023 | 0230 | October | 6544 | 5453 | 1400 | 0 | -3735 | -3735 | -2445 | Critical Branch | Critical Branch | 1091 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT
20231023 | 0330 | October | 6664 | 5523 | 1400 | 0 | -2691 | -2691 | -1476 | Critical Branch | Critical Branch | 1141 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT
20231023 | 0430 | October | 6664 | 5523 | 1400 | 0 | -2691 | -2691 | -1476 | Critical Branch | Critical Branch | 1141 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT
20231023 | 0530 | October | 6664 | 5523 | 1400 | 0 | -2691 | -2691 | -1476 | Critical Branch | Critical Branch | 1141 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT
20231023 | 0630 | October | 6664 | 5523 | 1400 | 0 | -2691 | -2691 | -1476 | Critical Branch | Critical Branch | 1141 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT
20231023 | 0730 | October | 6928 | 5742 | 1400 | 0 | -2264 | -2264 | -1082 | Critical Branch | Validation phase | 1186 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT |  |  |  | CH | 6682 | Expected overloading on the following CNEC: CNE: 380kV Filisur - Sils , C: N-2 ALBERTVILLE-RONDISSONE
20231023 | 0830 | October | 6928 | 5742 | 1400 | 0 | -2264 | -2264 | -1082 | Critical Branch | Validation phase | 1186 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT |  |  |  | CH | 6682 | Expected overloading on the following CNEC: CNE: 380kV Filisur - Sils , C: N-2 ALBERTVILLE-RONDISSONE
20231023 | 0930 | October | 6650 | 5608 | 1400 | 0 | -2920 | -2920 | -1992 | Critical Branch | Critical Branch | 1042 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT
20231023 | 1030 | October | 6650 | 5608 | 1400 | 0 | -2920 | -2920 | -1992 | Critical Branch | Critical Branch | 1042 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT
20231023 | 1130 | October | 6650 | 5608 | 1400 | 0 | -2920 | -2920 | -1992 | Critical Branch | Critical Branch | 1042 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT
20231023 | 1230 | October | 5923 | 5170 | 1400 | 0 | -2819 | -2819 | -2140 | Critical Branch | Critical Branch | 753 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT
20231023 | 1330 | October | 5923 | 5170 | 1400 | 0 | -2819 | -2819 | -2140 | Critical Branch | Critical Branch | 753 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT
20231023 | 1430 | October | 5923 | 5170 | 1400 | 0 | -2819 | -2819 | -2140 | Critical Branch | Critical Branch | 753 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT
20231023 | 1530 | October | 6662 | 5615 | 1400 | 0 | -3982 | -3982 | -2871 | Critical Branch | Critical Branch | 1047 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT
20231023 | 1630 | October | 6662 | 5615 | 1400 | 0 | -3982 | -3982 | -2871 | Critical Branch | Critical Branch | 1047 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT
20231023 | 1730 | October | 6662 | 5615 | 1400 | 0 | -3982 | -3982 | -2871 | Critical Branch | Critical Branch | 1047 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT
20231023 | 1830 | October | 6770 | 5665 | 1400 | 0 | -3540 | -3540 | -2374 | Critical Branch | Validation phase | 1105 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT |  |  |  | CH | 6555 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231023 | 1930 | October | 6770 | 5665 | 1400 | 0 | -3540 | -3540 | -2374 | Critical Branch | Validation phase | 1105 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT |  |  |  | CH | 6555 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231023 | 2030 | October | 6770 | 5665 | 1400 | 0 | -3540 | -3540 | -2374 | Critical Branch | Validation phase | 1105 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT |  |  |  | CH | 6555 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231023 | 2130 | October | 6683 | 5612 | 1400 | 0 | -2626 | -2626 | -1608 | Critical Branch | Validation phase | 1071 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT |  |  |  | CH | 6467 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231023 | 2230 | October | 6683 | 5612 | 1400 | 0 | -2626 | -2626 | -1608 | Critical Branch | Validation phase | 1071 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT |  |  |  | CH | 6467 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231023 | 2330 | October | 6088 | 5169 | 1400 | 0 | -2032 | -2032 | -1162 | Critical Branch | Validation phase | 919 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT |  |  |  | CH | 5872 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231025 | 0030 | October | 6623 | 5906 | 1400 | 0 | -3152 | -3152 | -2374 | Critical Branch | Critical Branch | 717 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE - RONDISSONE | AT | 0 | Reduction because NTC over thermal limit on border
20231025 | 0130 | October | 6623 | 5906 | 1400 | 0 | -3152 | -3152 | -2374 | Critical Branch | Critical Branch | 717 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE - RONDISSONE | AT | 0 | Reduction because NTC over thermal limit on border
20231025 | 0230 | October | 6623 | 5906 | 1400 | 0 | -3152 | -3152 | -2374 | Critical Branch | Critical Branch | 717 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE - RONDISSONE | AT | 0 | Reduction because NTC over thermal limit on border
20231025 | 0330 | October | 6544 | 5854 | 1400 | 0 | -1232 | -1232 | -638 | Critical Branch | Critical Branch | 690 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE - RONDISSONE | AT | 0 | Reduction because NTC over thermal limit on border
20231025 | 0430 | October | 6544 | 5854 | 1400 | 0 | -1232 | -1232 | -638 | Critical Branch | Critical Branch | 690 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE - RONDISSONE | AT | 0 | Reduction because NTC over thermal limit on border
20231025 | 0530 | October | 6544 | 5854 | 1400 | 0 | -1232 | -1232 | -638 | Critical Branch | Critical Branch | 690 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE - RONDISSONE | AT | 0 | Reduction because NTC over thermal limit on border
20231025 | 0630 | October | 6544 | 5854 | 1400 | 0 | -1232 | -1232 | -638 | Critical Branch | Critical Branch | 690 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE - RONDISSONE | AT | 0 | Reduction because NTC over thermal limit on border
20231025 | 0730 | October | 6479 | 5871 | 1400 | 0 | -1705 | -1705 | -1181 | Critical Branch | Critical Branch | 608 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE - RONDISSONE | AT | 0 | Reduction because NTC over thermal limit on border
20231025 | 0830 | October | 6479 | 5871 | 1400 | 0 | -1705 | -1705 | -1181 | Critical Branch | Critical Branch | 608 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE - RONDISSONE | AT | 0 | Reduction because NTC over thermal limit on border
20231025 | 0930 | October | 6522 | 5891 | 1400 | 0 | -469 | -469 | 48 | Critical Branch | Validation phase | 631 | 48 | FR | 1400 | Bilateral - N-2 ALBERTVILLE - RONDISSONE | AT | 0 | Reduction because NTC over thermal limit on border | CH | 6320 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231025 | 1030 | October | 6522 | 5891 | 1400 | 0 | -469 | -469 | 48 | Critical Branch | Validation phase | 631 | 48 | FR | 1400 | Bilateral - N-2 ALBERTVILLE - RONDISSONE | AT | 0 | Reduction because NTC over thermal limit on border | CH | 6320 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231025 | 1130 | October | 6522 | 5891 | 1400 | 0 | -469 | -469 | 48 | Critical Branch | Validation phase | 631 | 48 | FR | 1400 | Bilateral - N-2 ALBERTVILLE - RONDISSONE | AT | 0 | Reduction because NTC over thermal limit on border | CH | 6320 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231025 | 1230 | October | 5983 | 5529 | 1400 | 0 | -4467 | -4467 | -3996 | Critical Branch | Validation phase | 454 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE - RONDISSONE | AT | 0 | Reduction because NTC over thermal limit on border | CH | 5775 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231025 | 1330 | October | 5983 | 5529 | 1400 | 0 | -4467 | -4467 | -3996 | Critical Branch | Validation phase | 454 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE - RONDISSONE | AT | 0 | Reduction because NTC over thermal limit on border | CH | 5775 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231025 | 1430 | October | 5983 | 5529 | 1400 | 0 | -4467 | -4467 | -3996 | Critical Branch | Validation phase | 454 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE - RONDISSONE | AT | 0 | Reduction because NTC over thermal limit on border | CH | 5775 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231025 | 1530 | October | 6571 | 5873 | 1400 | 0 | -2276 | -2276 | -1577 | Critical Branch | Validation phase | 698 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE - RONDISSONE | AT | 0 | Reduction because NTC over thermal limit on border | CH | 6293 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231025 | 1630 | October | 6571 | 5873 | 1400 | 0 | -2276 | -2276 | -1577 | Critical Branch | Validation phase | 698 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE - RONDISSONE | AT | 0 | Reduction because NTC over thermal limit on border | CH | 6293 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231025 | 1730 | October | 6811 | 6114 | 1400 | 243 | -2499 | -2499 | -1800 | Critical Branch | Validation phase | 697 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE - RONDISSONE | AT | 246 | Reduction because NTC over thermal limit on border | CH | 6533 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231025 | 1830 | October | 6970 | 6210 | 1400 | 248 | -4265 | -4265 | -3485 | Critical Branch | Validation phase | 760 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE - RONDISSONE | AT | 252 | Reduction because NTC over thermal limit on border | CH | 6674 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231025 | 1930 | October | 6970 | 6210 | 1400 | 248 | -4265 | -4265 | -3485 | Critical Branch | Validation phase | 760 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE - RONDISSONE | AT | 252 | Reduction because NTC over thermal limit on border | CH | 6674 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231025 | 2030 | October | 6970 | 6210 | 1400 | 248 | -4265 | -4265 | -3485 | Critical Branch | Validation phase | 760 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE - RONDISSONE | AT | 252 | Reduction because NTC over thermal limit on border | CH | 6674 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231025 | 2130 | October | 7080 | 6284 | 1400 | 253 | -4403 | -4403 | -3544 | Critical Branch | Validation phase | 796 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE - RONDISSONE | AT | 257 | Reduction because NTC over thermal limit on border | CH | 6784 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231025 | 2230 | October | 7080 | 6284 | 1400 | 253 | -4403 | -4403 | -3544 | Critical Branch | Validation phase | 796 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE - RONDISSONE | AT | 257 | Reduction because NTC over thermal limit on border | CH | 6784 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231025 | 2330 | October | 6470 | 5819 | 1400 | 238 | -3802 | -3802 | -3098 | Critical Branch | Validation phase | 651 | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE - RONDISSONE | AT | 242 | Reduction because NTC over thermal limit on border | CH | 6174 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231026 | 0030 | October | 7170 | 5689 | 1400 | 225 | -992 | -992 | 403 | Critical Branch | Validation phase | 1481 | 403 | FR | 1400 | Bilateral - N-2 Albertville Rondissone / Albertvillee-Grande Ile | AT | 225 | Reduction because NTC over thermal limit on border | IT | 5988 | Load Flow not convergent
20231026 | 0130 | October | 7170 | 5689 | 1400 | 225 | -992 | -992 | 403 | Critical Branch | Validation phase | 1481 | 403 | FR | 1400 | Bilateral - N-2 Albertville Rondissone / Albertvillee-Grande Ile | AT | 225 | Reduction because NTC over thermal limit on border | IT | 5988 | Load Flow not convergent
20231026 | 0230 | October | 7170 | 5689 | 1400 | 225 | -992 | -992 | 403 | Critical Branch | Validation phase | 1481 | 403 | FR | 1400 | Bilateral - N-2 Albertville Rondissone / Albertvillee-Grande Ile | AT | 225 | Reduction because NTC over thermal limit on border | IT | 5988 | Load Flow not convergent
20231026 | 0330 | October | 6323 | 5602 | 1400 | 225 | -3352 | -3352 | -2558 | Critical Branch | Validation phase | 721 | 0 | FR | 1400 | Bilateral - N-2 Albertville Rondissone / Albertvillee-Grande Ile | AT | 225 | Reduction because NTC over thermal limit on border | IT | 5850 | Load Flow not convergent
20231026 | 0430 | October | 6323 | 5602 | 1400 | 225 | -3352 | -3352 | -2558 | Critical Branch | Validation phase | 721 | 0 | FR | 1400 | Bilateral - N-2 Albertville Rondissone / Albertvillee-Grande Ile | AT | 225 | Reduction because NTC over thermal limit on border | IT | 5850 | Load Flow not convergent
20231026 | 0530 | October | 6323 | 5602 | 1400 | 225 | -3352 | -3352 | -2558 | Critical Branch | Validation phase | 721 | 0 | FR | 1400 | Bilateral - N-2 Albertville Rondissone / Albertvillee-Grande Ile | AT | 225 | Reduction because NTC over thermal limit on border | IT | 5850 | Load Flow not convergent
20231026 | 0630 | October | 6323 | 5602 | 1400 | 225 | -3352 | -3352 | -2558 | Critical Branch | Validation phase | 721 | 0 | FR | 1400 | Bilateral - N-2 Albertville Rondissone / Albertvillee-Grande Ile | AT | 225 | Reduction because NTC over thermal limit on border | IT | 5850 | Load Flow not convergent
20231026 | 0730 | October | 6780 | 5550 | 1400 | 210 | -3569 | -3569 | -2362 | Critical Branch | Validation phase | 1230 | 0 | FR | 1400 | Bilateral - N-2 Albertville Rondissone / Albertvillee-Grande Ile | AT | 240 | Reduction because NTC over thermal limit on border | IT | 5700 | N-1 ABV-RON2 -> ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231026 | 0830 | October | 6780 | 5550 | 1400 | 210 | -3569 | -3569 | -2362 | Critical Branch | Validation phase | 1230 | 0 | FR | 1400 | Bilateral - N-2 Albertville Rondissone / Albertvillee-Grande Ile | AT | 240 | Reduction because NTC over thermal limit on border | IT | 5700 | N-1 ABV-RON2 -&gt; ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231026 | 0930 | October | 6853 | 5550 | 1400 | 210 | -4206 | -4206 | -2839 | Critical Branch | Validation phase | 1303 | 0 | FR | 1400 | Bilateral - N-2 Albertville Rondissone / Albertvillee-Grande Ile | AT | 240 | Reduction because NTC over thermal limit on border | IT | 5700 | N-1 ABV-RON2 -&gt; ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231026 | 1030 | October | 6853 | 5550 | 1400 | 210 | -4206 | -4206 | -2839 | Critical Branch | Validation phase | 1303 | 0 | FR | 1400 | Bilateral - N-2 Albertville Rondissone / Albertvillee-Grande Ile | AT | 240 | Reduction because NTC over thermal limit on border | IT | 5700 | N-1 ABV-RON2 -&gt; ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231026 | 1130 | October | 6853 | 5550 | 1400 | 210 | -4206 | -4206 | -2839 | Critical Branch | Validation phase | 1303 | 0 | FR | 1400 | Bilateral - N-2 Albertville Rondissone / Albertvillee-Grande Ile | AT | 240 | Reduction because NTC over thermal limit on border | IT | 5700 | N-1 ABV-RON2 -&gt; ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231026 | 1230 | October | 6366 | 5550 | 1400 | 210 | -9634 | -9634 | -8966 | Critical Branch | Validation phase | 816 | 0 | FR | 1400 | Bilateral - N-2 Albertville Rondissone / Albertvillee-Grande Ile | AT | 240 | Reduction because NTC over thermal limit on border | IT | 5700 | N-1 ABV-RON2 -&gt; ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231026 | 1330 | October | 6366 | 5550 | 1400 | 210 | -9634 | -9634 | -8966 | Critical Branch | Validation phase | 816 | 0 | FR | 1400 | Bilateral - N-2 Albertville Rondissone / Albertvillee-Grande Ile | AT | 240 | Reduction because NTC over thermal limit on border | IT | 5700 | N-1 ABV-RON2 -&gt; ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231026 | 1430 | October | 6366 | 5550 | 1400 | 210 | -9634 | -9634 | -8966 | Critical Branch | Validation phase | 816 | 0 | FR | 1400 | Bilateral - N-2 Albertville Rondissone / Albertvillee-Grande Ile | AT | 240 | Reduction because NTC over thermal limit on border | IT | 5700 | N-1 ABV-RON2 -&gt; ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231026 | 1530 | October | 6930 | 5550 | 1400 | 210 | -2429 | -2429 | -1050 | Critical Branch | Validation phase | 1380 | 0 | FR | 1400 | Bilateral - N-2 Albertville Rondissone / Albertvillee-Grande Ile | AT | 240 | Reduction because NTC over thermal limit on border | IT | 5700 | N-1 ABV-RON2 -&gt; ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231026 | 1630 | October | 6930 | 5550 | 1400 | 210 | -2429 | -2429 | -1050 | Critical Branch | Validation phase | 1380 | 0 | FR | 1400 | Bilateral - N-2 Albertville Rondissone / Albertvillee-Grande Ile | AT | 240 | Reduction because NTC over thermal limit on border | IT | 5700 | N-1 ABV-RON2 -&gt; ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231026 | 1730 | October | 6930 | 5550 | 1400 | 210 | -2429 | -2429 | -1050 | Critical Branch | Validation phase | 1380 | 0 | FR | 1400 | Bilateral - N-2 Albertville Rondissone / Albertvillee-Grande Ile | AT | 240 | Reduction because NTC over thermal limit on border | IT | 5700 | N-1 ABV-RON2 -&gt; ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231026 | 1830 | October | 6953 | 5550 | 1400 | 210 | -1968 | -1968 | -609 | Critical Branch | Validation phase | 1403 | 0 | FR | 1400 | Bilateral - N-2 Albertville Rondissone / Albertvillee-Grande Ile | AT | 240 | Reduction because NTC over thermal limit on border | IT | 5700 | N-1 ABV-RON2 -&gt; ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231026 | 1930 | October | 6953 | 5550 | 1400 | 210 | -1968 | -1968 | -609 | Critical Branch | Validation phase | 1403 | 0 | FR | 1400 | Bilateral - N-2 Albertville Rondissone / Albertvillee-Grande Ile | AT | 240 | Reduction because NTC over thermal limit on border | IT | 5700 | N-1 ABV-RON2 -&gt; ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231026 | 2030 | October | 6953 | 5550 | 1400 | 210 | -1968 | -1968 | -609 | Critical Branch | Validation phase | 1403 | 0 | FR | 1400 | Bilateral - N-2 Albertville Rondissone / Albertvillee-Grande Ile | AT | 240 | Reduction because NTC over thermal limit on border | IT | 5700 | N-1 ABV-RON2 -&gt; ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231026 | 2130 | October | 6770 | 5550 | 1400 | 210 | -3367 | -3367 | -2166 | Critical Branch | Validation phase | 1220 | 0 | FR | 1400 | Bilateral - N-2 Albertville Rondissone / Albertvillee-Grande Ile | AT | 240 | Reduction because NTC over thermal limit on border | IT | 5700 | N-1 ABV-RON2 -&gt; ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231026 | 2230 | October | 6770 | 5550 | 1400 | 210 | -3367 | -3367 | -2166 | Critical Branch | Validation phase | 1220 | 0 | FR | 1400 | Bilateral - N-2 Albertville Rondissone / Albertvillee-Grande Ile | AT | 240 | Reduction because NTC over thermal limit on border | IT | 5700 | N-1 ABV-RON2 -&gt; ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231026 | 2330 | October | 6160 | 5502 | 1400 | 219 | -2758 | -2758 | -2123 | Critical Branch | Validation phase | 658 | 0 | FR | 1400 | Bilateral - N-2 Albertville Rondissone / Albertvillee-Grande Ile | AT | 225 | Reduction because NTC over thermal limit on border | IT | 5700 | N-1 ABV-RON2 -&gt; ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231027 | 0030 | October | 6928 | 5527 | 1400 | 220 | -3025 | -3025 | -1656 | Critical Branch | Validation phase | 1401 | 0 | FR | 1400 | Bilateral - N-2 Alberville-Rondissonne / Cornier Riddes |  |  |  | IT | 5738 | N-1 ABV-RON2 -> ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231027 | 0130 | October | 6928 | 5527 | 1400 | 220 | -3025 | -3025 | -1656 | Critical Branch | Validation phase | 1401 | 0 | FR | 1400 | Bilateral - N-2 Alberville-Rondissonne / Cornier-Riddes |  |  |  | IT | 5738 | N-1 ABV-RON2 -> ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231027 | 0230 | October | 6928 | 5527 | 1400 | 220 | -3025 | -3025 | -1656 | Critical Branch | Validation phase | 1401 | 0 | FR | 1400 | Bilateral - N-2 Alberville-Rondissonne / Cornier Riddes |  |  |  | IT | 5738 | N-1 ABV-RON2 -> ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231027 | 0330 | October | 6835 | 5465 | 1400 | 217 | -3567 | -3567 | -2122 | Critical Branch | Validation phase | 1370 | 0 | FR | 1400 | Bilateral - N-2 Alberville-Rondissonne / Cornier Riddes |  |  |  | IT | 5645 | N-1 ABV-RON2 -> ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231027 | 0430 | October | 6835 | 5465 | 1400 | 217 | -3567 | -3567 | -2122 | Critical Branch | Validation phase | 1370 | 0 | FR | 1400 | Bilateral - N-2 Alberville-Rondissonne / Cornier Riddes |  |  |  | IT | 5645 | N-1 ABV-RON2 -> ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231027 | 0530 | October | 6835 | 5465 | 1400 | 217 | -3567 | -3567 | -2122 | Critical Branch | Validation phase | 1370 | 0 | FR | 1400 | Bilateral - N-2 Alberville-Rondissonne / Cornier Riddes |  |  |  | IT | 5645 | N-1 ABV-RON2 -> ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231027 | 0630 | October | 6835 | 5465 | 1400 | 217 | -3567 | -3567 | -2122 | Critical Branch | Validation phase | 1370 | 0 | FR | 1400 | Bilateral - N-2 Alberville-Rondissonne / Cornier Riddes |  |  |  | IT | 5645 | N-1 ABV-RON2 -> ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231027 | 0730 | October | 6956 | 5595 | 1400 | 213 | -1485 | -1485 | -184 | Critical Branch | Validation phase | 1361 | 0 | FR | 1400 | Bilateral - N-2 Alberville-Rondissonne / Cornier Riddes |  |  |  | IT | 5766 | N-1 ABV-RON2 -> ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231027 | 0830 | October | 6956 | 5595 | 1400 | 213 | -1485 | -1485 | -184 | Critical Branch | Validation phase | 1361 | 0 | FR | 1400 | Bilateral - N-2 Alberville-Rondissonne / Cornier Riddes |  |  |  | IT | 5766 | N-1 ABV-RON2 -> ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231027 | 0930 | October | 6899 | 5556 | 1400 | 211 | -3470 | -3470 | -2106 | Critical Branch | Validation phase | 1343 | 0 | FR | 1400 | Bilateral - N-2 Alberville-Rondissonne / Cornier Riddes |  |  |  | IT | 5709 | N-1 ABV-RON2 -> ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231027 | 1030 | October | 6899 | 5556 | 1400 | 211 | -3470 | -3470 | -2106 | Critical Branch | Validation phase | 1343 | 0 | FR | 1400 | Bilateral - N-2 Alberville-Rondissonne / Cornier Riddes |  |  |  | IT | 5709 | N-1 ABV-RON2 -> ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231027 | 1130 | October | 6899 | 5556 | 1400 | 211 | -3470 | -3470 | -2106 | Critical Branch | Validation phase | 1343 | 0 | FR | 1400 | Bilateral - N-2 Alberville-Rondissonne / Cornier Riddes |  |  |  | IT | 5709 | N-1 ABV-RON2 -> ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231027 | 1230 | October | 6961 | 5598 | 1400 | 213 | -3571 | -3571 | -2121 | Critical Branch | Validation phase | 1363 | 0 | FR | 1400 | Bilateral - N-2 Alberville-Rondissonne / Cornier Riddes |  |  |  | IT | 5771 | N-1 ABV-RON2 -> ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231027 | 1330 | October | 6961 | 5598 | 1400 | 213 | -3571 | -3571 | -2121 | Critical Branch | Validation phase | 1363 | 0 | FR | 1400 | Bilateral - N-2 Alberville-Rondissonne / Cornier Riddes |  |  |  | IT | 5771 | N-1 ABV-RON2 -> ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231027 | 1430 | October | 6961 | 5598 | 1400 | 213 | -3571 | -3571 | -2121 | Critical Branch | Validation phase | 1363 | 0 | FR | 1400 | Bilateral - N-2 Alberville-Rondissonne / Cornier Riddes |  |  |  | IT | 5771 | N-1 ABV-RON2 -> ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231027 | 1530 | October | 7139 | 5583 | 1400 | 212 | -4467 | -4467 | -2889 | Critical Branch | Validation phase | 1556 | 0 | FR | 1400 | Bilateral - N-2 Alberville-Rondissonne / Cornier Riddes |  |  |  | IT | 5749 | N-1 ABV-RON2 -> ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231027 | 1630 | October | 7139 | 5583 | 1400 | 212 | -4467 | -4467 | -2889 | Critical Branch | Validation phase | 1556 | 0 | FR | 1400 | Bilateral - N-2 Alberville-Rondissonne / Cornier Riddes |  |  |  | IT | 5749 | N-1 ABV-RON2 -> ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231027 | 1730 | October | 8439 | 5939 | 2398 | 175 | -5820 | -5820 | -3320 | Critical Branch | Validation phase | 2500 | 0 | IT | 5749 | N-1 ABV-RON2 -> ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231027 | 1830 | October | 8228 | 6628 | 2702 | 197 | -1984 | -1984 | -384 | Critical Branch | Validation phase | 1600 | 0 | IT | 6438 | N-1 ABV-RON2 -> ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231027 | 1930 | October | 8228 | 6628 | 2702 | 197 | -1984 | -1984 | -384 | Critical Branch | Validation phase | 1600 | 0 | IT | 6438 | N-1 ABV-RON2 -> ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231027 | 2030 | October | 8228 | 6628 | 2702 | 197 | -1984 | -1984 | -384 | Critical Branch | Validation phase | 1600 | 0 | IT | 6438 | N-1 ABV-RON2 -> ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231027 | 2130 | October | 8469 | 6769 | 2764 | 202 | -1230 | -1230 | 470 | Critical Branch | Validation phase | 1700 | 470 | IT | 6579 | N-1 ABV-RON2 -> ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231027 | 2230 | October | 8469 | 6769 | 2764 | 202 | -1230 | -1230 | 470 | Critical Branch | Validation phase | 1700 | 470 | IT | 6579 | N-1 ABV-RON2 -> ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231027 | 2330 | October | 7859 | 6759 | 2871 | 206 | -588 | -588 | 512 | Critical Branch | Validation phase | 1100 | 512 | IT | 6569 | N-1 ABV-RON2 -> ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231028 | 0030 | October | 8054 | 7654 | 3282 | 235 | -2974 | -2974 | -2574 | Critical Branch | Validation phase | 400 | 0 | IT | 7464 | N-1 ABV-RON2 -> ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231028 | 0130 | October | 8054 | 7654 | 3282 | 235 | -2974 | -2974 | -2574 | Critical Branch | Validation phase | 400 | 0 | IT | 7464 | N-1 ABV-RON2 -> ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231028 | 0230 | October | 8054 | 7654 | 3282 | 235 | -2974 | -2974 | -2574 | Critical Branch | Validation phase | 400 | 0 | IT | 7464 | N-1 ABV-RON2 -> ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231028 | 0330 | October | 8034 | 7634 | 3273 | 235 | -3517 | -3517 | -3117 | Critical Branch | Validation phase | 400 | 0 | IT | 7444 | N-1 ABV-RON2 -> ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231028 | 0430 | October | 8034 | 7634 | 3273 | 235 | -3517 | -3517 | -3117 | Critical Branch | Validation phase | 400 | 0 | IT | 7444 | N-1 ABV-RON2 -> ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231028 | 0530 | October | 8034 | 7634 | 3273 | 235 | -3517 | -3517 | -3117 | Critical Branch | Validation phase | 400 | 0 | IT | 7444 | N-1 ABV-RON2 -> ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231028 | 0630 | October | 8034 | 7634 | 3273 | 235 | -3517 | -3517 | -3117 | Critical Branch | Validation phase | 400 | 0 | IT | 7444 | N-1 ABV-RON2 -> ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231028 | 0730 | October | 7675 | 7330 | 3012 | 220 | -4394 | -4394 | -4049 | Critical Branch | Validation phase | 345 | 0 | CH | 7140 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231028 | 0830 | October | 7675 | 7330 | 3012 | 220 | -4394 | -4394 | -4049 | Critical Branch | Validation phase | 345 | 0 | CH | 7140 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231028 | 1230 | October | 8303 | 7603 | 3132 | 229 | -1579 | -1579 | -879 | Critical Branch | Validation phase | 700 | 0 | IT | 7413 | N-1 ABV-RON2 -> ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231028 | 1330 | October | 8303 | 7603 | 3132 | 229 | -1579 | -1579 | -879 | Critical Branch | Validation phase | 700 | 0 | IT | 7413 | N-1 ABV-RON2 -> ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231028 | 1430 | October | 8303 | 7603 | 3132 | 229 | -1579 | -1579 | -879 | Critical Branch | Validation phase | 700 | 0 | IT | 7413 | N-1 ABV-RON2 -> ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231028 | 1830 | October | 8123 | 7409 | 3046 | 223 | -4144 | -4144 | -3430 | Critical Branch | Validation phase | 714 | 0 | CH | 7219 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Pradella-Robbia + Filisur-Robbia
20231028 | 1930 | October | 8123 | 7409 | 3046 | 223 | -4144 | -4144 | -3430 | Critical Branch | Validation phase | 714 | 0 | CH | 7219 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Pradella-Robbia + Filisur-Robbia
20231028 | 2030 | October | 8123 | 7409 | 3046 | 223 | -4144 | -4144 | -3430 | Critical Branch | Validation phase | 714 | 0 | CH | 7219 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Pradella-Robbia + Filisur-Robbia
20231028 | 2130 | October | 7813 | 7571 | 3118 | 228 | -1935 | -1935 | -1693 | Critical Branch | Validation phase | 242 | 0 | CH | 7381 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Pradella-Robbia + Filisur-Robbia
20231028 | 2230 | October | 7813 | 7571 | 3118 | 228 | -1935 | -1935 | -1693 | Critical Branch | Validation phase | 242 | 0 | CH | 7381 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Pradella-Robbia + Filisur-Robbia
20231028 | 2330 | October | 7203 | 6961 | 2964 | 213 | -1300 | -1300 | -1058 | Critical Branch | Validation phase | 242 | 0 | CH | 6771 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Pradella-Robbia + Filisur-Robbia
20231030 | 0030 | October | 7877 | 7121 | 3038 | 218 | -3599 | -3599 | -2843 | Critical Branch | Validation phase | 756 | 0 | CH | 6931 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231030 | 0130 | October | 7877 | 7121 | 3038 | 218 | -3599 | -3599 | -2843 | Critical Branch | Validation phase | 756 | 0 | CH | 6931 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231030 | 0230 | October | 7877 | 7121 | 3038 | 218 | -3599 | -3599 | -2843 | Critical Branch | Validation phase | 756 | 0 | CH | 6931 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231030 | 0330 | October | 7395 | 7190 | 3069 | 220 | -1215 | -1215 | -1010 | Critical Branch | Validation phase | 205 | 0 | IT | 7000 | ABV-GRA1/2 -&gt; ABV-GRA3, ABV-RON1 on ABV-RON2 and viceversa
20231030 | 0430 | October | 7395 | 7190 | 3069 | 220 | -1215 | -1215 | -1010 | Critical Branch | Validation phase | 205 | 0 | IT | 7000 | ABV-GRA1/2 -&gt; ABV-GRA3, ABV-RON1 on ABV-RON2 and viceversa
20231030 | 0530 | October | 7395 | 7190 | 3069 | 220 | -1215 | -1215 | -1010 | Critical Branch | Validation phase | 205 | 0 | IT | 7000 | ABV-GRA1/2 -&gt; ABV-GRA3, ABV-RON1 on ABV-RON2 and viceversa
20231030 | 0630 | October | 7395 | 7190 | 3069 | 220 | -1215 | -1215 | -1010 | Critical Branch | Validation phase | 205 | 0 | IT | 7000 | ABV-GRA1/2 -&gt; ABV-GRA3, ABV-RON1 on ABV-RON2 and viceversa
20231030 | 1230 | October | 8094 | 7033 | 2881 | 210 | -1079 | -1079 | -18 | Critical Branch | Validation phase | 1061 | 0 | CH | 6843 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231030 | 1330 | October | 8094 | 7033 | 2881 | 210 | -1079 | -1079 | -18 | Critical Branch | Validation phase | 1061 | 0 | CH | 6843 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231030 | 1430 | October | 8094 | 7033 | 2881 | 210 | -1079 | -1079 | -18 | Critical Branch | Validation phase | 1061 | 0 | CH | 6843 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231030 | 1530 | October | 8067 | 6962 | 2849 | 208 | -1444 | -1444 | -339 | Critical Branch | Validation phase | 1105 | 0 | CH | 6772 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231030 | 1630 | October | 8067 | 6962 | 2849 | 208 | -1444 | -1444 | -339 | Critical Branch | Validation phase | 1105 | 0 | CH | 6772 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231030 | 1730 | October | 8067 | 6962 | 2849 | 208 | -1444 | -1444 | -339 | Critical Branch | Validation phase | 1105 | 0 | CH | 6772 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231030 | 1830 | October | 7713 | 6926 | 2833 | 207 | -2204 | -2204 | -1417 | Critical Branch | Validation phase | 787 | 0 | CH | 6736 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231030 | 1930 | October | 7713 | 6926 | 2833 | 207 | -2204 | -2204 | -1417 | Critical Branch | Validation phase | 787 | 0 | CH | 6736 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231030 | 2030 | October | 7713 | 6926 | 2833 | 207 | -2204 | -2204 | -1417 | Critical Branch | Validation phase | 787 | 0 | CH | 6736 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231030 | 2130 | October | 8115 | 7071 | 2897 | 212 | -3498 | -3498 | -2454 | Critical Branch | Validation phase | 1044 | 0 | CH | 6881 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231030 | 2230 | October | 8115 | 7071 | 2897 | 212 | -3498 | -3498 | -2454 | Critical Branch | Validation phase | 1044 | 0 | CH | 6881 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231030 | 2330 | October | 7505 | 6461 | 2735 | 196 | -2897 | -2897 | -1853 | Critical Branch | Validation phase | 1044 | 0 | CH | 6271 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231031 | 0030 | October | 7486 | 7190 | 3069 | 220 | -3169 | -3169 | -2873 | Critical Branch | Validation phase | 296 | 0 | IT | 7000 | N-2 ABV - RON on 220 kV grid
20231031 | 0130 | October | 7486 | 7190 | 3069 | 220 | -3169 | -3169 | -2873 | Critical Branch | Validation phase | 296 | 0 | IT | 7000 | N-2 ABV - RON on 220 kV grid
20231031 | 0230 | October | 7486 | 7190 | 3069 | 220 | -3169 | -3169 | -2873 | Critical Branch | Validation phase | 296 | 0 | IT | 7000 | N-2 ABV - RON on 220 kV grid
20231031 | 0330 | October | 7300 | 7190 | 3069 | 220 | -4839 | -4839 | -4729 | Critical Branch | Validation phase | 110 | 0 | IT | 7000 | N-2 ABV - RON on 220 kV grid
20231031 | 0430 | October | 7300 | 7190 | 3069 | 220 | -4839 | -4839 | -4729 | Critical Branch | Validation phase | 110 | 0 | IT | 7000 | N-2 ABV - RON on 220 kV grid
20231031 | 0530 | October | 7300 | 7190 | 3069 | 220 | -4839 | -4839 | -4729 | Critical Branch | Validation phase | 110 | 0 | IT | 7000 | N-2 ABV - RON on 220 kV grid
20231031 | 0630 | October | 7300 | 7190 | 3069 | 220 | -4839 | -4839 | -4729 | Critical Branch | Validation phase | 110 | 0 | IT | 7000 | N-2 ABV - RON on 220 kV grid
20231031 | 0730 | October | 7877 | 7227 | 2966 | 217 | -1752 | -1752 | -1102 | Critical Branch | Validation phase | 650 | 0 | CH | 7037 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231031 | 0830 | October | 7877 | 7227 | 2966 | 217 | -1752 | -1752 | -1102 | Critical Branch | Validation phase | 650 | 0 | CH | 7037 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231031 | 1530 | October | 7715 | 7676 | 3164 | 231 | -1779 | -1779 | -1740 | Critical Branch | Validation phase | 39 | 0 | CH | 7486 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231031 | 1630 | October | 7715 | 7676 | 3164 | 231 | -1779 | -1779 | -1740 | Critical Branch | Validation phase | 39 | 0 | CH | 7486 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231031 | 1730 | October | 7715 | 7676 | 3164 | 231 | -1779 | -1779 | -1740 | Critical Branch | Validation phase | 39 | 0 | CH | 7486 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231031 | 1830 | October | 7497 | 7484 | 3080 | 225 | -2165 | -2165 | -2152 | Critical Branch | Validation phase | 13 | 0 | CH | 7294 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231031 | 1930 | October | 7497 | 7484 | 3080 | 225 | -2165 | -2165 | -2152 | Critical Branch | Validation phase | 13 | 0 | CH | 7294 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231031 | 2030 | October | 7497 | 7484 | 3080 | 225 | -2165 | -2165 | -2152 | Critical Branch | Validation phase | 13 | 0 | CH | 7294 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231031 | 2130 | October | 7821 | 7367 | 3028 | 221 | -1228 | -1228 | -774 | Critical Branch | Validation phase | 454 | 0 | CH | 7177 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231031 | 2230 | October | 7821 | 7367 | 3028 | 221 | -1228 | -1228 | -774 | Critical Branch | Validation phase | 454 | 0 | CH | 7177 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231031 | 2330 | October | 7211 | 6757 | 2871 | 206 | -587 | -587 | -133 | Critical Branch | Validation phase | 454 | 0 | CH | 6567 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231101 | 0730 | November | 8040 | 7640 | 3634 | 213 |  |  |  | Scheduled TTC | Validation phase | 400 | 0 | CH | 7450 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231101 | 0830 | November | 8040 | 7640 | 3634 | 213 |  |  |  | Scheduled TTC | Validation phase | 400 | 0 | CH | 7450 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231101 | 0930 | November | 7545 | 7490 | 3558 | 209 | -1809 | -1809 | -1754 | Critical Branch | Validation phase | 55 | 0 | CH | 7300 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231101 | 1030 | November | 7545 | 7490 | 3558 | 209 | -1809 | -1809 | -1754 | Critical Branch | Validation phase | 55 | 0 | CH | 7300 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231101 | 1130 | November | 7545 | 7490 | 3558 | 209 | -1809 | -1809 | -1754 | Critical Branch | Validation phase | 55 | 0 | CH | 7300 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231101 | 1530 | November | 8040 | 7640 | 3634 | 213 |  |  |  | Scheduled TTC | Validation phase | 400 | 0 | CH | 7450 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231101 | 1630 | November | 8040 | 7640 | 3634 | 213 |  |  |  | Scheduled TTC | Validation phase | 400 | 0 | CH | 7450 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231101 | 1730 | November | 8040 | 7640 | 3634 | 213 |  |  |  | Scheduled TTC | Validation phase | 400 | 0 | CH | 7450 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231101 | 1830 | November | 8040 | 7640 | 3634 | 213 |  |  |  | Scheduled TTC | Validation phase | 400 | 0 | CH | 7450 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231101 | 1930 | November | 8040 | 7640 | 3634 | 213 |  |  |  | Scheduled TTC | Validation phase | 400 | 0 | CH | 7450 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231101 | 2030 | November | 8040 | 7640 | 3634 | 213 |  |  |  | Scheduled TTC | Validation phase | 400 | 0 | CH | 7450 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231101 | 2130 | November | 8040 | 7640 | 3634 | 213 |  |  |  | Scheduled TTC | Validation phase | 400 | 0 | CH | 7450 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231101 | 2230 | November | 8040 | 7640 | 3634 | 213 |  |  |  | Scheduled TTC | Validation phase | 400 | 0 | CH | 7450 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231101 | 2330 | November | 8040 | 7640 | 3634 | 213 |  |  |  | Scheduled TTC | Validation phase | 400 | 0 | CH | 7450 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231102 | 0030 | November | 7304 | 7275 | 3108 | 223 | -490 | -490 | -461 | Critical Branch | Validation phase | 29 | 0 | CH | 7085 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231102 | 0130 | November | 7304 | 7275 | 3108 | 223 | -490 | -490 | -461 | Critical Branch | Validation phase | 29 | 0 | CH | 7085 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231102 | 0230 | November | 7304 | 7275 | 3108 | 223 | -490 | -490 | -461 | Critical Branch | Validation phase | 29 | 0 | CH | 7085 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231102 | 0730 | November | 6594 | 6199 | 2549 | 104 | -1360 | -1360 | -965 | TTC Selection - LTTC | Validation phase | 395 | 0 | CH | 6009 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231102 | 0830 | November | 6594 | 6199 | 2549 | 104 | -1360 | -1360 | -965 | TTC Selection - LTTC | Validation phase | 395 | 0 | CH | 6009 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231102 | 0930 | November | 7844 | 6199 | 2549 | 104 |  |  |  | Scheduled TTC | Validation phase | 1645 | 0 | CH | 6009 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231102 | 1030 | November | 7844 | 6199 | 2549 | 104 |  |  |  | Scheduled TTC | Validation phase | 1645 | 0 | CH | 6009 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231102 | 1130 | November | 7844 | 6199 | 2549 | 104 |  |  |  | Scheduled TTC | Validation phase | 1645 | 0 | CH | 6009 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231102 | 1230 | November | 6594 | 6160 | 2532 | 103 | -397 | -397 | 37 | TTC Selection - LTTC | Validation phase | 434 | 37 | CH | 5970 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231102 | 1330 | November | 6594 | 6160 | 2532 | 103 | -397 | -397 | 37 | TTC Selection - LTTC | Validation phase | 434 | 37 | CH | 5970 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231102 | 1430 | November | 6594 | 6160 | 2532 | 103 | -397 | -397 | 37 | TTC Selection - LTTC | Validation phase | 434 | 37 | CH | 5970 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231103 | 0930 | November | 7575 | 6990 | 2903 | 118 | -2922 | -2922 | -2337 | Critical Branch | Validation phase | 585 | 0 | IT | 6800 | ABV-GRA1-2 on ABV-GRA 3 and ABV-RON 1-2 on VNS-VLR
20231103 | 1030 | November | 7575 | 6990 | 2903 | 118 | -2922 | -2922 | -2337 | Critical Branch | Validation phase | 585 | 0 | IT | 6800 | ABV-GRA1-2 on ABV-GRA 3 and ABV-RON 1-2 on VNS-VLR
20231103 | 1130 | November | 7575 | 6990 | 2903 | 118 | -2922 | -2922 | -2337 | Critical Branch | Validation phase | 585 | 0 | IT | 6800 | ABV-GRA1-2 on ABV-GRA 3 and ABV-RON 1-2 on VNS-VLR
20231103 | 1230 | November | 7119 | 6990 | 2903 | 118 | -2293 | -2293 | -2164 | Critical Branch | Validation phase | 129 | 0 | IT | 6800 | ABV-GRA1-2 on ABV-GRA 3 and ABV-RON 1-2 on VNS-VLR
20231103 | 1330 | November | 7119 | 6990 | 2903 | 118 | -2293 | -2293 | -2164 | Critical Branch | Validation phase | 129 | 0 | IT | 6800 | ABV-GRA1-2 on ABV-GRA 3 and ABV-RON 1-2 on VNS-VLR
20231103 | 1430 | November | 7119 | 6990 | 2903 | 118 | -2293 | -2293 | -2164 | Critical Branch | Validation phase | 129 | 0 | IT | 6800 | ABV-GRA1-2 on ABV-GRA 3 and ABV-RON 1-2 on VNS-VLR
20231103 | 1530 | November | 7521 | 6990 | 2903 | 118 | -3531 | -3531 | -3000 | Critical Branch | Validation phase | 531 | 0 | IT | 6800 | ABV-GRA1-2 on ABV-GRA 3 and ABV-RON 1-2 on VNS-VLR
20231104 | 0330 | November | 7597 | 7278 | 2937 | 233 | 505 | 505 | 265 | Minimum Margin | Minimum Margin | 319 | 265 | FR | 2937 | Bilateral - NTC Secure due to Process fail during TSO validation phase
20231104 | 0430 | November | 7597 | 7278 | 2937 | 233 | 505 | 505 | 265 | Minimum Margin | Minimum Margin | 319 | 265 | FR | 2937 | Bilateral - NTC Secure due to Process fail during TSO validation phase
20231104 | 0530 | November | 7597 | 7278 | 2937 | 233 | 505 | 505 | 265 | Minimum Margin | Minimum Margin | 319 | 265 | FR | 2937 | Bilateral - NTC Secure due to Process fail during TSO validation phase
20231104 | 0630 | November | 7597 | 7278 | 2937 | 233 | 505 | 505 | 265 | Minimum Margin | Minimum Margin | 319 | 265 | FR | 2937 | Bilateral - NTC Secure due to Process fail during TSO validation phase
20231104 | 0730 | November | 7295 | 7241 | 2972 | 217 | -834 | -834 | -780 | Critical Branch | Validation phase | 54 | 0 | CH | 7051 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231104 | 0830 | November | 7295 | 7241 | 2972 | 217 | -834 | -834 | -780 | Critical Branch | Validation phase | 54 | 0 | CH | 7051 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231104 | 1230 | November | 7410 | 7106 | 2743 | 223 | 682 | 498 | 432 | Minimum Margin | Minimum Margin | 304 | 248 | FR | 2743 | Bilateral - NTC Secure due to Process fail during TSO validation phase
20231104 | 1330 | November | 7410 | 7106 | 2743 | 223 | 682 | 498 | 432 | Minimum Margin | Minimum Margin | 304 | 248 | FR | 2743 | Bilateral - NTC Secure due to Process fail during TSO validation phase
20231104 | 1430 | November | 7410 | 7106 | 2743 | 223 | 682 | 498 | 432 | Minimum Margin | Minimum Margin | 304 | 248 | FR | 2743 | Bilateral - NTC Secure due to Process fail during TSO validation phase
20231104 | 1530 | November | 6949 | 6908 | 2826 | 206 | -786 | -786 | -745 | Critical Branch | Validation phase | 41 | 0 | CH | 6718 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231104 | 1630 | November | 6949 | 6908 | 2826 | 206 | -786 | -786 | -745 | Critical Branch | Validation phase | 41 | 0 | CH | 6718 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231104 | 1730 | November | 8349 | 8250 | 2877 | 210 | -2405 | -2405 | -2306 | Critical Branch | Validation phase | 99 | 0 | CH | 8060 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231104 | 1830 | November | 8521 | 8421 | 2940 | 215 | -2373 | -2373 | -2273 | Critical Branch | Validation phase | 100 | 0 | CH | 8231 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231104 | 1930 | November | 8521 | 8421 | 2940 | 215 | -2373 | -2373 | -2273 | Critical Branch | Validation phase | 100 | 0 | CH | 8231 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231104 | 2030 | November | 8521 | 8421 | 2940 | 215 | -2373 | -2373 | -2273 | Critical Branch | Validation phase | 100 | 0 | CH | 8231 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231104 | 2130 | November | 8691 | 8590 | 3003 | 219 | -2068 | -2068 | -1967 | Critical Branch | Validation phase | 101 | 0 | CH | 8400 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231104 | 2230 | November | 8691 | 8590 | 3003 | 219 | -2068 | -2068 | -1967 | Critical Branch | Validation phase | 101 | 0 | CH | 8400 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231105 | 0030 | November | 8540 | 7740 | 2826 | 203 |  |  |  | Scheduled TTC | Validation phase | 800 | 0 | IT | 7550 | ABV-GRA1-2 on ABV-GRA 3 and ABV-RON 1-2 on VNS-VLR
20231105 | 0130 | November | 8540 | 7740 | 2826 | 203 |  |  |  | Scheduled TTC | Validation phase | 800 | 0 | IT | 7550 | ABV-GRA1-2 on ABV-GRA 3 and ABV-RON 1-2 on VNS-VLR
20231105 | 0230 | November | 8540 | 7740 | 2826 | 203 |  |  |  | Scheduled TTC | Validation phase | 800 | 0 | IT | 7550 | ABV-GRA1-2 on ABV-GRA 3 and ABV-RON 1-2 on VNS-VLR
20231105 | 0330 | November | 8540 | 7740 | 2826 | 203 |  |  |  | Scheduled TTC | Validation phase | 800 | 0 | IT | 7550 | ABV-GRA1-2 on ABV-GRA 3 and ABV-RON 1-2 on VNS-VLR
20231105 | 0430 | November | 8540 | 7740 | 2826 | 203 |  |  |  | Scheduled TTC | Validation phase | 800 | 0 | IT | 7550 | ABV-GRA1-2 on ABV-GRA 3 and ABV-RON 1-2 on VNS-VLR
20231105 | 0530 | November | 8540 | 7740 | 2826 | 203 |  |  |  | Scheduled TTC | Validation phase | 800 | 0 | IT | 7550 | ABV-GRA1-2 on ABV-GRA 3 and ABV-RON 1-2 on VNS-VLR
20231105 | 0630 | November | 8540 | 7740 | 2826 | 203 |  |  |  | Scheduled TTC | Validation phase | 800 | 0 | IT | 7550 | ABV-GRA1-2 on ABV-GRA 3 and ABV-RON 1-2 on VNS-VLR
20231105 | 0730 | November | 8540 | 7740 | 2826 | 203 |  |  |  | Scheduled TTC | Validation phase | 800 | 0 | IT | 7550 | ABV-GRA1-2 on ABV-GRA 3 and ABV-RON 1-2 on VNS-VLR
20231105 | 0830 | November | 8540 | 7740 | 2826 | 203 |  |  |  | Scheduled TTC | Validation phase | 800 | 0 | IT | 7550 | ABV-GRA1-2 on ABV-GRA 3 and ABV-RON 1-2 on VNS-VLR
20231105 | 0930 | November | 8410 | 7610 | 2775 | 199 | -2069 | -2069 | -1269 | Critical Branch | Validation phase | 800 | 0 | IT | 7420 | ABV-GRA1-2 on ABV-GRA 3 and ABV-RON 1-2 on VNS-VLR
20231105 | 1030 | November | 8410 | 7610 | 2775 | 199 | -2069 | -2069 | -1269 | Critical Branch | Validation phase | 800 | 0 | IT | 7420 | ABV-GRA1-2 on ABV-GRA 3 and ABV-RON 1-2 on VNS-VLR
20231105 | 1130 | November | 8410 | 7610 | 2775 | 199 | -2069 | -2069 | -1269 | Critical Branch | Validation phase | 800 | 0 | IT | 7420 | ABV-GRA1-2 on ABV-GRA 3 and ABV-RON 1-2 on VNS-VLR
20231105 | 1230 | November | 8586 | 7610 | 2775 | 199 | -2084 | -2084 | -1108 | Critical Branch | Validation phase | 976 | 0 | IT | 7420 | ABV-GRA1-2 on ABV-GRA 3 and ABV-RON 1-2 on VNS-VLR
20231105 | 1330 | November | 8586 | 7610 | 2775 | 199 | -2084 | -2084 | -1108 | Critical Branch | Validation phase | 976 | 0 | IT | 7420 | ABV-GRA1-2 on ABV-GRA 3 and ABV-RON 1-2 on VNS-VLR
20231105 | 1430 | November | 8586 | 7610 | 2775 | 199 | -2084 | -2084 | -1108 | Critical Branch | Validation phase | 976 | 0 | IT | 7420 | ABV-GRA1-2 on ABV-GRA 3 and ABV-RON 1-2 on VNS-VLR
20231105 | 1530 | November | 8540 | 7740 | 2826 | 203 |  |  |  | Scheduled TTC | Validation phase | 800 | 0 | IT | 7550 | ABV-GRA1-2 on ABV-GRA 3 and ABV-RON 1-2 on VNS-VLR
20231105 | 1630 | November | 8540 | 7740 | 2826 | 203 |  |  |  | Scheduled TTC | Validation phase | 800 | 0 | IT | 7550 | ABV-GRA1-2 on ABV-GRA 3 and ABV-RON 1-2 on VNS-VLR
20231105 | 1730 | November | 8540 | 7740 | 2826 | 203 |  |  |  | Scheduled TTC | Validation phase | 800 | 0 | IT | 7550 | ABV-GRA1-2 on ABV-GRA 3 and ABV-RON 1-2 on VNS-VLR
20231105 | 1830 | November | 8540 | 7740 | 2826 | 203 |  |  |  | Scheduled TTC | Validation phase | 800 | 0 | IT | 7550 | ABV-GRA1-2 on ABV-GRA 3 and ABV-RON 1-2 on VNS-VLR
20231105 | 1930 | November | 8540 | 7740 | 2826 | 203 |  |  |  | Scheduled TTC | Validation phase | 800 | 0 | IT | 7550 | ABV-GRA1-2 on ABV-GRA 3 and ABV-RON 1-2 on VNS-VLR
20231105 | 2030 | November | 8540 | 7740 | 2826 | 203 |  |  |  | Scheduled TTC | Validation phase | 800 | 0 | IT | 7550 | ABV-GRA1-2 on ABV-GRA 3 and ABV-RON 1-2 on VNS-VLR
20231105 | 2130 | November | 8540 | 7740 | 2826 | 203 |  |  |  | Scheduled TTC | Validation phase | 800 | 0 | IT | 7550 | ABV-GRA1-2 on ABV-GRA 3 and ABV-RON 1-2 on VNS-VLR
20231105 | 2230 | November | 8540 | 7740 | 2826 | 203 |  |  |  | Scheduled TTC | Validation phase | 800 | 0 | IT | 7550 | ABV-GRA1-2 on ABV-GRA 3 and ABV-RON 1-2 on VNS-VLR
20231105 | 2330 | November | 8540 | 7740 | 2826 | 203 |  |  |  | Scheduled TTC | Validation phase | 800 | 0 | IT | 7550 | ABV-GRA1-2 on ABV-GRA 3 and ABV-RON 1-2 on VNS-VLR
20231107 | 1530 | November | 8784 | 8422 | 3044 | 222 | -1971 | -1971 | -1609 | Critical Branch | Validation phase | 362 | 0 | CH | 8232 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Pradella-Robbia + Filisur-Robbia
20231107 | 1630 | November | 8784 | 8422 | 3044 | 222 | -1971 | -1971 | -1609 | Critical Branch | Validation phase | 362 | 0 | CH | 8232 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Pradella-Robbia + Filisur-Robbia
20231107 | 1730 | November | 9084 | 8522 | 2978 | 218 | -2309 | -2309 | -1747 | Critical Branch | Validation phase | 562 | 0 | CH | 8332 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Pradella-Robbia + Filisur-Robbia
20231107 | 1830 | November | 8255 | 8238 | 2872 | 210 | -2900 | -2900 | -2883 | Critical Branch | Validation phase | 17 | 0 | CH | 8048 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231107 | 1930 | November | 8255 | 8238 | 2872 | 210 | -2900 | -2900 | -2883 | Critical Branch | Validation phase | 17 | 0 | CH | 8048 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231107 | 2030 | November | 8255 | 8238 | 2872 | 210 | -2900 | -2900 | -2883 | Critical Branch | Validation phase | 17 | 0 | CH | 8048 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231107 | 2130 | November | 8697 | 8382 | 2926 | 214 | -2125 | -2125 | -1810 | Critical Branch | Validation phase | 315 | 0 | CH | 8192 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231107 | 2230 | November | 8697 | 8382 | 2926 | 214 | -2125 | -2125 | -1810 | Critical Branch | Validation phase | 315 | 0 | CH | 8192 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231107 | 2330 | November | 7887 | 7572 | 2760 | 198 | -1294 | -1294 | -979 | Critical Branch | Validation phase | 315 | 0 | CH | 7382 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231108 | 0730 | November | 8408 | 8346 | 3015 | 220 | -1426 | -1426 | -1364 | Critical Branch | Validation phase | 62 | 0 | CH | 8156 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231108 | 0830 | November | 8408 | 8346 | 3015 | 220 | -1426 | -1426 | -1364 | Critical Branch | Validation phase | 62 | 0 | CH | 8156 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231108 | 1530 | November | 8886 | 8786 | 3184 | 233 | -1547 | -1547 | -1447 | Critical Branch | Validation phase | 100 | 0 | CH | 8596 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231108 | 1630 | November | 8886 | 8786 | 3184 | 233 | -1547 | -1547 | -1447 | Critical Branch | Validation phase | 100 | 0 | CH | 8596 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231108 | 1730 | November | 9186 | 8786 | 3076 | 225 | -1904 | -1904 | -1504 | Critical Branch | Validation phase | 400 | 0 | CH | 8596 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231108 | 1830 | November | 9350 | 8850 | 3099 | 226 |  |  |  | Scheduled TTC | Validation phase | 500 | 0 | CH | 8660 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231108 | 1930 | November | 9350 | 8850 | 3099 | 226 |  |  |  | Scheduled TTC | Validation phase | 500 | 0 | CH | 8660 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231108 | 2030 | November | 9350 | 8850 | 3099 | 226 |  |  |  | Scheduled TTC | Validation phase | 500 | 0 | CH | 8660 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231110 | 0930 | November | 9050 | 8750 | 3170 | 232 |  |  |  | Scheduled TTC | Validation phase | 300 | 0 | IT | 8560 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo-Musignano, C: N-1 Soazza-Bulciago
20231110 | 1030 | November | 9050 | 8750 | 3170 | 232 |  |  |  | Scheduled TTC | Validation phase | 300 | 0 | IT | 8560 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo-Musignano, C: N-1 Soazza-Bulciago
20231110 | 1130 | November | 9050 | 8750 | 3170 | 232 |  |  |  | Scheduled TTC | Validation phase | 300 | 0 | IT | 8560 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo-Musignano, C: N-1 Soazza-Bulciago
20231110 | 1730 | November | 9044 | 8744 | 3060 | 224 | -3168 | -3168 | -2868 | Critical Branch | Validation phase | 300 | 0 | IT | 8554 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo-Musignano, C: N-1 Soazza-Bulciago
20231111 | 0030 | November | 8778 | 8264 | 3030 | 217 | -3122 | -3122 | -2608 | Critical Branch | Validation phase | 514 | 0 | CH | 8074 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231111 | 0130 | November | 8778 | 8264 | 3030 | 217 | -3122 | -3122 | -2608 | Critical Branch | Validation phase | 514 | 0 | CH | 8074 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231111 | 0230 | November | 8778 | 8264 | 3030 | 217 | -3122 | -3122 | -2608 | Critical Branch | Validation phase | 514 | 0 | CH | 8074 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231111 | 0930 | November | 8634 | 7633 | 2741 | 200 | -2171 | -2171 | -1170 | Critical Branch | Validation phase | 1001 | 0 | CH | 7443 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231111 | 1030 | November | 8634 | 7633 | 2741 | 200 | -2171 | -2171 | -1170 | Critical Branch | Validation phase | 1001 | 0 | CH | 7443 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231111 | 1130 | November | 8634 | 7633 | 2741 | 200 | -2171 | -2171 | -1170 | Critical Branch | Validation phase | 1001 | 0 | CH | 7443 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231111 | 1730 | November | 8100 | 7800 | 2710 | 198 | -2560 | -2560 | -2260 | TTC Selection - LTTC | Validation phase | 300 | 0 | IT | 7610 | Correct value IT issue
20231112 | 0030 | November | 8540 | 8101 | 2967 | 213 |  |  |  | Scheduled TTC | Validation phase | 439 | 0 | IT | 7911 | Computation Failed
20231112 | 0130 | November | 8540 | 8101 | 2967 | 213 |  |  |  | Scheduled TTC | Validation phase | 439 | 0 | IT | 7911 | Computation Failed
20231112 | 0230 | November | 8540 | 8101 | 2967 | 213 |  |  |  | Scheduled TTC | Validation phase | 439 | 0 | IT | 7911 | Computation Failed
20231112 | 1730 | November | 8664 | 7464 | 2548 | 183 | -4174 | -4174 | -2974 | Critical Branch | Validation phase | 1200 | 0 | IT | 7274 | Correct value IT issue
20231112 | 1830 | November | 9076 | 8300 | 2854 | 205 |  |  |  | Scheduled TTC | Validation phase | 776 | 0 | CH | 8110 | Lavorgo-Musignano N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231112 | 1930 | November | 9076 | 8300 | 2854 | 205 |  |  |  | Scheduled TTC | Validation phase | 776 | 0 | CH | 8110 | Lavorgo-Musignano N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231112 | 2030 | November | 9076 | 8300 | 2854 | 205 |  |  |  | Scheduled TTC | Validation phase | 776 | 0 | CH | 8110 | Lavorgo-Musignano N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231113 | 1730 | November | 8712 | 8412 | 2545 | 256 | -3463 | -3463 | -3163 | Critical Branch | Validation phase | 300 | 0 | IT | 8222 | Correct value IT issue
20231114 | 0030 | November | 9135 | 7737 | 2269 | 225 | -357 | -357 | 1040 | Critical Branch | Validation phase | 1398 | 1040 | AT | 225 | Bilateral - Reduction because of outage of line 912 |  |  |  | CH | 7550 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231114 | 0130 | November | 9135 | 7737 | 2269 | 225 | -357 | -357 | 1040 | Critical Branch | Validation phase | 1398 | 1040 | AT | 225 | Bilateral - Reduction because of outage of line 912 |  |  |  | CH | 7550 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231114 | 0230 | November | 9135 | 7737 | 2269 | 225 | -357 | -357 | 1040 | Critical Branch | Validation phase | 1398 | 1040 | AT | 225 | Bilateral - Reduction because of outage of line 912 |  |  |  | CH | 7550 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231114 | 0330 | November | 8734 | 7718 | 2263 | 225 | -2975 | -2975 | -1960 | Critical Branch | Validation phase | 1016 | 0 | AT | 225 | Bilateral - Reduction because of outage of line 912 |  |  |  | CH | 7531 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-1 AVISE-RIDDES
20231114 | 0430 | November | 8734 | 7718 | 2263 | 225 | -2975 | -2975 | -1960 | Critical Branch | Validation phase | 1016 | 0 | AT | 225 | Bilateral - Reduction because of outage of line 912 |  |  |  | CH | 7531 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-1 AVISE-RIDDES
20231114 | 0530 | November | 8734 | 7718 | 2263 | 225 | -2975 | -2975 | -1960 | Critical Branch | Validation phase | 1016 | 0 | AT | 225 | Bilateral - Reduction because of outage of line 912 |  |  |  | CH | 7531 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-1 AVISE-RIDDES
20231114 | 0630 | November | 8734 | 7718 | 2263 | 225 | -2975 | -2975 | -1960 | Critical Branch | Validation phase | 1016 | 0 | AT | 225 | Bilateral - Reduction because of outage of line 912 |  |  |  | CH | 7531 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-1 AVISE-RIDDES
20231114 | 0730 | November | 8513 | 7812 | 2280 | 229 | -1467 | -1467 | -766 | Critical Branch | Validation phase | 701 | 0 | CH | 7622 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231114 | 0830 | November | 8513 | 7812 | 2280 | 229 | -1467 | -1467 | -766 | Critical Branch | Validation phase | 701 | 0 | CH | 7622 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231114 | 0930 | November | 8889 | 8040 | 2351 | 237 | -1152 | -1152 | -303 | Critical Branch | Validation phase | 849 | 0 | CH | 7850 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231114 | 1030 | November | 8889 | 8040 | 2351 | 237 | -1152 | -1152 | -303 | Critical Branch | Validation phase | 849 | 0 | CH | 7850 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231114 | 1130 | November | 8889 | 8040 | 2351 | 237 | -1152 | -1152 | -303 | Critical Branch | Validation phase | 849 | 0 | CH | 7850 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231115 | 0030 | November | 8363 | 8340 | 2465 | 225 | -2473 | -2473 | -2454 | Critical Branch | Critical Branch | 23 | 0 | AT | 225 | Bilateral - Reduction because of outage of line 912
20231115 | 0130 | November | 8363 | 8340 | 2465 | 225 | -2473 | -2473 | -2454 | Critical Branch | Critical Branch | 23 | 0 | AT | 225 | Bilateral - Reduction because of outage of line 912
20231115 | 0230 | November | 8363 | 8340 | 2465 | 225 | -2473 | -2473 | -2454 | Critical Branch | Critical Branch | 23 | 0 | AT | 225 | Bilateral - Reduction because of outage of line 912
20231115 | 0330 | November | 8548 | 8519 | 2522 | 225 | -3791 | -3791 | -3766 | Critical Branch | Critical Branch | 29 | 0 | AT | 225 | Bilateral - Reduction because of outage of line 912
20231115 | 0430 | November | 8548 | 8519 | 2522 | 225 | -3791 | -3791 | -3766 | Critical Branch | Critical Branch | 29 | 0 | AT | 225 | Bilateral - Reduction because of outage of line 912
20231115 | 0530 | November | 8548 | 8519 | 2522 | 225 | -3791 | -3791 | -3766 | Critical Branch | Critical Branch | 29 | 0 | AT | 225 | Bilateral - Reduction because of outage of line 912
20231115 | 0630 | November | 8548 | 8519 | 2522 | 225 | -3791 | -3791 | -3766 | Critical Branch | Critical Branch | 29 | 0 | AT | 225 | Bilateral - Reduction because of outage of line 912
20231115 | 0730 | November | 8743 | 8724 | 2570 | 240 | -1205 | -1205 | -1188 | Critical Branch | Critical Branch | 19 | 0 | AT | 240 | Bilateral - Reduction because of outage of line 912
20231115 | 0830 | November | 8743 | 8724 | 2570 | 240 | -1205 | -1205 | -1188 | Critical Branch | Critical Branch | 19 | 0 | AT | 240 | Bilateral - Reduction because of outage of line 912
20231115 | 0930 | November | 8900 | 8876 | 2619 | 240 | -2605 | -2605 | -2585 | Critical Branch | Critical Branch | 24 | 0 | AT | 240 | Bilateral - Reduction because of outage of line 912
20231115 | 1030 | November | 8900 | 8876 | 2619 | 240 | -2605 | -2605 | -2585 | Critical Branch | Critical Branch | 24 | 0 | AT | 240 | Bilateral - Reduction because of outage of line 912
20231115 | 1130 | November | 8900 | 8876 | 2619 | 240 | -2605 | -2605 | -2585 | Critical Branch | Critical Branch | 24 | 0 | AT | 240 | Bilateral - Reduction because of outage of line 912
20231115 | 1230 | November | 8629 | 8614 | 2534 | 240 | -3117 | -3117 | -3105 | Critical Branch | Critical Branch | 15 | 0 | AT | 240 | Bilateral - Reduction because of outage of line 912
20231115 | 1330 | November | 8629 | 8614 | 2534 | 240 | -3117 | -3117 | -3105 | Critical Branch | Critical Branch | 15 | 0 | AT | 240 | Bilateral - Reduction because of outage of line 912
20231115 | 1430 | November | 8629 | 8614 | 2534 | 240 | -3117 | -3117 | -3105 | Critical Branch | Critical Branch | 15 | 0 | AT | 240 | Bilateral - Reduction because of outage of line 912
20231115 | 1530 | November | 8668 | 8652 | 2547 | 240 | -4081 | -4081 | -4067 | Critical Branch | Critical Branch | 16 | 0 | AT | 240 | Bilateral - Reduction because of outage of line 912
20231115 | 1630 | November | 8668 | 8652 | 2547 | 240 | -4081 | -4081 | -4067 | Critical Branch | Critical Branch | 16 | 0 | AT | 240 | Bilateral - Reduction because of outage of line 912
20231115 | 1730 | November | 9868 | 9854 | 3477 | 240 | -5287 | -5287 | -5275 | Critical Branch | Critical Branch | 14 | 0 | AT | 240 | Bilateral - Reduction because of outage of line 912
20231116 | 0930 | November | 9132 | 8873 | 3216 | 237 | -2206 | -2206 | -1947 | Critical Branch | Validation phase | 259 | 0 | CH | 8598 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231116 | 1030 | November | 9132 | 8873 | 3216 | 237 | -2206 | -2206 | -1947 | Critical Branch | Validation phase | 259 | 0 | CH | 8598 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231116 | 1130 | November | 9132 | 8873 | 3216 | 237 | -2206 | -2206 | -1947 | Critical Branch | Validation phase | 259 | 0 | CH | 8598 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231116 | 1730 | November | 9364 | 9064 | 3178 | 235 | -3522 | -3522 | -3222 | Critical Branch | Validation phase | 300 | 0 | CH | 8789 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231117 | 1530 | November | 9203 | 9003 | 3267 | 239 | -2123 | -2123 | -1923 | Critical Branch | Validation phase | 200 | 0 | CH | 8728 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231117 | 1630 | November | 9203 | 9003 | 3267 | 239 | -2123 | -2123 | -1923 | Critical Branch | Validation phase | 200 | 0 | CH | 8728 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231117 | 1730 | November | 9503 | 9003 | 3155 | 234 | -2462 | -2462 | -1962 | Critical Branch | Validation phase | 500 | 0 | CH | 8728 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231117 | 2130 | November | 9290 | 9090 | 3188 | 235 | -2679 | -2679 | -2479 | Critical Branch | Validation phase | 200 | 0 | CH | 8815 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231117 | 2230 | November | 9290 | 9090 | 3188 | 235 | -2680 | -2680 | -2480 | Critical Branch | Validation phase | 200 | 0 | CH | 8820 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231118 | 0030 | November | 8843 | 8443 | 3100 | 223 | -5913 | -5913 | -5513 | Critical Branch | Validation phase | 400 | 0 | IT | 8173 | N-1 ABV-RON1 ->ABV-RON2
20231118 | 0130 | November | 8843 | 8443 | 3100 | 223 | -5913 | -5913 | -5513 | Critical Branch | Validation phase | 400 | 0 | IT | 8173 | N-1 ABV-RON1 -&gt;ABV-RON2
20231118 | 0230 | November | 8843 | 8443 | 3100 | 223 | -5913 | -5913 | -5513 | Critical Branch | Validation phase | 400 | 0 | IT | 8173 | N-1 ABV-RON1 -&gt;ABV-RON2
20231118 | 0930 | November | 9178 | 8778 | 3179 | 235 | -3055 | -3055 | -2655 | Critical Branch | Validation phase | 400 | 0 | IT | 8503 | N-1 ABV-RON1 ->ABV-RON2
20231118 | 1030 | November | 9178 | 8778 | 3179 | 235 | -3055 | -3055 | -2655 | Critical Branch | Validation phase | 400 | 0 | IT | 8503 | N-1 ABV-RON1 -&gt;ABV-RON2
20231118 | 1130 | November | 9178 | 8778 | 3179 | 235 | -3055 | -3055 | -2655 | Critical Branch | Validation phase | 400 | 0 | IT | 8503 | N-1 ABV-RON1 -&gt;ABV-RON2
20231118 | 1230 | November | 9079 | 8778 | 3179 | 235 | -1536 | -1536 | -1235 | Critical Branch | Validation phase | 301 | 0 | IT | 8503 | N-1 ABV-RON1 -&gt;ABV-RON2
20231118 | 1330 | November | 9079 | 8778 | 3179 | 235 | -1536 | -1536 | -1235 | Critical Branch | Validation phase | 301 | 0 | IT | 8503 | N-1 ABV-RON1 -&gt;ABV-RON2
20231118 | 1430 | November | 9079 | 8778 | 3179 | 235 | -1536 | -1536 | -1235 | Critical Branch | Validation phase | 301 | 0 | IT | 8503 | N-1 ABV-RON1 -&gt;ABV-RON2
20231118 | 1530 | November | 9153 | 8778 | 3179 | 235 | -2559 | -2559 | -2184 | Critical Branch | Validation phase | 375 | 0 | IT | 8503 | N-1 ABV-RON1 -&gt;ABV-RON2
20231118 | 1630 | November | 9153 | 8778 | 3179 | 235 | -2559 | -2559 | -2184 | Critical Branch | Validation phase | 375 | 0 | IT | 8503 | N-1 ABV-RON1 -&gt;ABV-RON2
20231118 | 1730 | November | 9453 | 8778 | 3071 | 230 | -2904 | -2904 | -2229 | Critical Branch | Validation phase | 675 | 0 | IT | 8503 | N-1 ABV-RON1 -&gt;ABV-RON2
20231119 | 1730 | November | 9251 | 8375 | 2879 | 213 | -2667 | -2667 | -1791 | Critical Branch | Validation phase | 876 | 0 | IT | 8100 | N-2 ROB-SFI/GOR-ROB on BUL-SOA
20231119 | 1830 | November | 9536 | 8951 | 3092 | 223 | 568 | 535 | 618 | Minimum Margin | Validation phase | 585 | 585 | CH | 8676 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231119 | 1930 | November | 9536 | 8951 | 3092 | 223 | 568 | 535 | 618 | Minimum Margin | Validation phase | 585 | 585 | CH | 8676 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231119 | 2030 | November | 9536 | 8951 | 3092 | 223 | 568 | 535 | 618 | Minimum Margin | Validation phase | 585 | 585 | CH | 8676 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231119 | 2130 | November | 8784 | 8375 | 2879 | 213 | -1833 | -1833 | -1424 | Critical Branch | Validation phase | 409 | 0 | IT | 8100 | N-2 ROB-SFI/GOR-ROB on BUL-SOA
20231119 | 2230 | November | 8784 | 8370 | 2877 | 213 | -1834 | -1834 | -1420 | Critical Branch | Validation phase | 414 | 0 | IT | 8100 | N-2 ROB-SFI/GOR-ROB on BUL-SOA
20231120 | 0030 | November | 8540 | 8402 | 3000 | 225 |  |  |  | Scheduled TTC | Scheduled TTC | 138 | 0 | FR | 3000 | Bilateral - CREYS GENISSIAT
20231120 | 0130 | November | 8540 | 8402 | 3000 | 225 |  |  |  | Scheduled TTC | Scheduled TTC | 138 | 0 | FR | 3000 | Bilateral - CREYS GENISSIAT
20231120 | 0230 | November | 8540 | 8402 | 3000 | 225 |  |  |  | Scheduled TTC | Scheduled TTC | 138 | 0 | FR | 3000 | Bilateral - CREYS GENISSIAT
20231120 | 0330 | November | 8540 | 8402 | 3000 | 225 |  |  |  | Scheduled TTC | Scheduled TTC | 138 | 0 | FR | 3000 | Bilateral - CREYS GENISSIAT
20231120 | 0430 | November | 8540 | 8402 | 3000 | 225 |  |  |  | Scheduled TTC | Scheduled TTC | 138 | 0 | FR | 3000 | Bilateral - CREYS GENISSIAT
20231120 | 0530 | November | 8540 | 8402 | 3000 | 225 |  |  |  | Scheduled TTC | Scheduled TTC | 138 | 0 | FR | 3000 | Bilateral - CREYS GENISSIAT
20231120 | 0630 | November | 8540 | 7290 | 2645 | 203 |  |  |  | Scheduled TTC | Validation phase | 1250 | 0 | IT | 7015 | safe value
20231120 | 0730 | November | 8514 | 7264 | 2767 | 216 |  |  |  | Scheduled TTC | Validation phase | 1250 | 0 | IT | 6989 | safe value
20231120 | 0830 | November | 8514 | 7264 | 2767 | 216 |  |  |  | Scheduled TTC | Validation phase | 1250 | 0 | IT | 6989 | safe value
20231120 | 0930 | November | 8514 | 7264 | 2767 | 216 |  |  |  | Scheduled TTC | Validation phase | 1250 | 0 | IT | 6989 | safe value
20231120 | 1030 | November | 8514 | 7264 | 2767 | 216 |  |  |  | Scheduled TTC | Validation phase | 1250 | 0 | IT | 6989 | safe value
20231120 | 1130 | November | 8514 | 7264 | 2767 | 216 |  |  |  | Scheduled TTC | Validation phase | 1250 | 0 | IT | 6989 | safe value
20231120 | 1230 | November | 8514 | 7264 | 2767 | 216 |  |  |  | Scheduled TTC | Validation phase | 1250 | 0 | IT | 6989 | safe value
20231120 | 1330 | November | 8514 | 7264 | 2767 | 216 |  |  |  | Scheduled TTC | Validation phase | 1250 | 0 | IT | 6989 | safe value
20231120 | 1430 | November | 8514 | 7097 | 2600 | 216 |  |  |  | Scheduled TTC | Validation phase | 1417 | 0 | FR | 2600 | Bilateral - CREYS GENISSIAT |  |  |  | IT | 6989 | safe value
20231120 | 1530 | November | 8514 | 7097 | 2600 | 216 |  |  |  | Scheduled TTC | Validation phase | 1417 | 0 | FR | 2600 | Bilateral - CREYS GENISSIAT |  |  |  | IT | 6989 | safe value
20231120 | 1630 | November | 8514 | 7097 | 2600 | 216 |  |  |  | Scheduled TTC | Validation phase | 1417 | 0 | FR | 2600 | Bilateral - CREYS GENISSIAT |  |  |  | IT | 6989 | safe value
20231120 | 1730 | November | 8814 | 7378 | 2600 | 216 |  |  |  | Scheduled TTC | Validation phase | 1436 | 0 | FR | 2600 | Bilateral - CREYS GENISSIAT |  |  |  | IT | 7289 | safe value
20231120 | 1830 | November | 8814 | 7378 | 2600 | 216 |  |  |  | Scheduled TTC | Validation phase | 1436 | 0 | FR | 2600 | Bilateral - CREYS GENISSIAT |  |  |  | IT | 7289 | safe value
20231120 | 1930 | November | 8814 | 7378 | 2600 | 216 |  |  |  | Scheduled TTC | Validation phase | 1436 | 0 | FR | 2600 | Bilateral - CREYS GENISSIAT |  |  |  | IT | 7289 | safe value
20231120 | 2030 | November | 8814 | 7564 | 2786 | 216 |  |  |  | Scheduled TTC | Validation phase | 1250 | 0 | IT | 7289 | safe value
20231120 | 2130 | November | 8814 | 7564 | 2786 | 216 |  |  |  | Scheduled TTC | Validation phase | 1250 | 0 | IT | 7289 | safe value
20231120 | 2230 | November | 8814 | 7564 | 2786 | 216 |  |  |  | Scheduled TTC | Validation phase | 1250 | 0 | IT | 7294 | safe value
20231120 | 2330 | November | 8540 | 8202 | 2800 | 225 |  |  |  | Scheduled TTC | Scheduled TTC | 338 | 0 | FR | 2800 | Bilateral - CREYS GENISSIAT
20231121 | 0030 | November | 8540 | 8002 | 2600 | 225 |  |  |  | Scheduled TTC | Scheduled TTC | 538 | 0 | FR | 2600 | Bilateral - RDCR CREYS GENISSIAT N°1
20231121 | 0130 | November | 8540 | 8002 | 2600 | 225 |  |  |  | Scheduled TTC | Scheduled TTC | 538 | 0 | FR | 2600 | Bilateral - RDCR CREYS GENISSIAT N°1
20231121 | 0230 | November | 8540 | 8002 | 2600 | 225 |  |  |  | Scheduled TTC | Scheduled TTC | 538 | 0 | FR | 2600 | Bilateral - RDCR CREYS GENISSIAT N°1
20231121 | 0330 | November | 8540 | 8002 | 2600 | 225 |  |  |  | Scheduled TTC | Scheduled TTC | 538 | 0 | FR | 2600 | Bilateral - RDCR CREYS GENISSIAT N°1
20231121 | 0430 | November | 8540 | 8002 | 2600 | 225 |  |  |  | Scheduled TTC | Scheduled TTC | 538 | 0 | FR | 2600 | Bilateral - RDCR CREYS GENISSIAT N°1
20231121 | 0530 | November | 8540 | 8002 | 2600 | 225 |  |  |  | Scheduled TTC | Scheduled TTC | 538 | 0 | FR | 2600 | Bilateral - RDCR CREYS GENISSIAT N°1
20231121 | 0630 | November | 8540 | 8002 | 2600 | 225 |  |  |  | Scheduled TTC | Scheduled TTC | 538 | 0 | FR | 2600 | Bilateral - RDCR CREYS GENISSIAT N°1
20231121 | 0730 | November | 9050 | 8365 | 2600 | 240 |  |  |  | Scheduled TTC | Scheduled TTC | 685 | 0 | FR | 2600 | Bilateral - RDCR CREYS GENISSIAT N°1
20231121 | 0830 | November | 9050 | 8365 | 2600 | 240 |  |  |  | Scheduled TTC | Scheduled TTC | 685 | 0 | FR | 2600 | Bilateral - RDCR CREYS GENISSIAT N°1
20231121 | 0930 | November | 9050 | 8365 | 2600 | 240 |  |  |  | Scheduled TTC | Scheduled TTC | 685 | 0 | FR | 2600 | Bilateral - RDCR CREYS GENISSIAT N°1
20231121 | 1030 | November | 9050 | 8365 | 2600 | 240 |  |  |  | Scheduled TTC | Scheduled TTC | 685 | 0 | FR | 2600 | Bilateral - RDCR CREYS GENISSIAT N°1
20231121 | 1130 | November | 9050 | 8365 | 2600 | 240 |  |  |  | Scheduled TTC | Scheduled TTC | 685 | 0 | FR | 2600 | Bilateral - RDCR CREYS GENISSIAT N°1
20231121 | 1230 | November | 9050 | 8365 | 2600 | 240 |  |  |  | Scheduled TTC | Scheduled TTC | 685 | 0 | FR | 2600 | Bilateral - RDCR CREYS GENISSIAT N°1
20231121 | 1330 | November | 9050 | 8365 | 2600 | 240 |  |  |  | Scheduled TTC | Scheduled TTC | 685 | 0 | FR | 2600 | Bilateral - RDCR CREYS GENISSIAT N°1
20231121 | 1430 | November | 9050 | 8365 | 2600 | 240 |  |  |  | Scheduled TTC | Scheduled TTC | 685 | 0 | FR | 2600 | Bilateral - RDCR CREYS GENISSIAT N°1
20231121 | 1530 | November | 9050 | 8365 | 2600 | 240 |  |  |  | Scheduled TTC | Scheduled TTC | 685 | 0 | FR | 2600 | Bilateral - RDCR CREYS GENISSIAT N°1
20231121 | 1630 | November | 9050 | 8365 | 2600 | 240 |  |  |  | Scheduled TTC | Scheduled TTC | 685 | 0 | FR | 2600 | Bilateral - RDCR CREYS GENISSIAT N°1
20231121 | 1730 | November | 9350 | 8665 | 2600 | 240 |  |  |  | Scheduled TTC | Scheduled TTC | 685 | 0 | FR | 2600 | Bilateral - RDCR CREYS GENISSIAT N°1
20231121 | 1830 | November | 9350 | 8665 | 2600 | 240 |  |  |  | Scheduled TTC | Scheduled TTC | 685 | 0 | FR | 2600 | Bilateral - RDCR CREYS GENISSIAT N°1
20231121 | 1930 | November | 9350 | 8665 | 2600 | 240 |  |  |  | Scheduled TTC | Scheduled TTC | 685 | 0 | FR | 2600 | Bilateral - RDCR CREYS GENISSIAT N°1
20231121 | 2030 | November | 9350 | 8665 | 2600 | 240 |  |  |  | Scheduled TTC | Scheduled TTC | 685 | 0 | FR | 2600 | Bilateral - RDCR CREYS GENISSIAT N°1
20231121 | 2130 | November | 9350 | 8665 | 2600 | 240 |  |  |  | Scheduled TTC | Scheduled TTC | 685 | 0 | FR | 2600 | Bilateral - RDCR CREYS GENISSIAT N°1
20231121 | 2230 | November | 9350 | 8665 | 2600 | 240 |  |  |  | Scheduled TTC | Scheduled TTC | 685 | 0 | FR | 2600 | Bilateral - RDCR CREYS GENISSIAT N°1
20231121 | 2330 | November | 8540 | 8002 | 2600 | 225 |  |  |  | Scheduled TTC | Scheduled TTC | 538 | 0 | FR | 2600 | Bilateral - RDCR CREYS GENISSIAT N°1
20231122 | 0030 | November | 8576 | 8024 | 2600 | 226 | -2134 | -2134 | -1653 | Critical Branch | Critical Branch | 552 | 0 | FR | 2600 | Bilateral - RDCR CORNIER GENISSIAT
20231122 | 0130 | November | 8576 | 8024 | 2600 | 226 | -2134 | -2134 | -1653 | Critical Branch | Critical Branch | 552 | 0 | FR | 2600 | Bilateral - RDCR CORNIER GENISSIAT
20231122 | 0230 | November | 8576 | 8024 | 2600 | 226 | -2134 | -2134 | -1653 | Critical Branch | Critical Branch | 552 | 0 | FR | 2600 | Bilateral - RDCR CORNIER GENISSIAT
20231122 | 0330 | November | 8206 | 7800 | 2600 | 219 | -2168 | -2168 | -1613 | Critical Branch | Critical Branch | 406 | 0 | FR | 2600 | Bilateral - RDCR CORNIER GENISSIAT
20231122 | 0430 | November | 8206 | 7800 | 2600 | 219 | -2168 | -2168 | -1613 | Critical Branch | Critical Branch | 406 | 0 | FR | 2600 | Bilateral - RDCR CORNIER GENISSIAT
20231122 | 0530 | November | 8206 | 7800 | 2600 | 219 | -2168 | -2168 | -1613 | Critical Branch | Critical Branch | 406 | 0 | FR | 2600 | Bilateral - RDCR CORNIER GENISSIAT
20231122 | 0630 | November | 8206 | 7800 | 2600 | 219 | -2167 | -2167 | -1612 | Critical Branch | Critical Branch | 406 | 0 | FR | 2600 | Bilateral - RDCR CORNIER GENISSIAT
20231123 | 0030 | November | 8713 | 8313 | 2449 | 246 | -1974 | -1974 | -1574 | Critical Branch | Validation phase | 400 | 0 | IT | 8123 | N-2 380 kV ABV-RON 1&2 -> 380 kV PRA-VLR
20231123 | 0130 | November | 8713 | 8313 | 2449 | 246 | -1974 | -1974 | -1574 | Critical Branch | Validation phase | 400 | 0 | IT | 8123 | N-2 380 kV ABV-RON 1&amp;2 -&gt; 380 kV PRA-VLR
20231123 | 0230 | November | 8713 | 8313 | 2449 | 246 | -1974 | -1974 | -1574 | Critical Branch | Validation phase | 400 | 0 | IT | 8123 | N-2 380 kV ABV-RON 1&amp;2 -&gt; 380 kV PRA-VLR
20231123 | 0930 | November | 7916 | 7662 | 2233 | 225 | -254 | -254 | 0 | Critical Branch | Validation phase | 254 | 0 | IT | 7472 | N-2 380 kV ABV-GRA1&amp;2 -&gt; 380 kV ABV-GRA3
20231123 | 1030 | November | 7916 | 7662 | 2233 | 225 | -254 | -254 | 0 | Critical Branch | Validation phase | 254 | 0 | IT | 7472 | N-2 380 kV ABV-GRA1&2 -> 380 kV ABV-GRA3
20231123 | 1130 | November | 7916 | 7662 | 2233 | 225 | -254 | -254 | 0 | Critical Branch | Validation phase | 254 | 0 | IT | 7472 | N-2 380 kV ABV-GRA1&amp;2 -&gt; 380 kV ABV-GRA3
20231123 | 1730 | November | 7881 | 7662 | 2149 | 216 | -1399 | -1399 | -1180 | Critical Branch | Validation phase | 219 | 0 | IT | 7472 | N-2 380 kV ABV-GRA1&amp;amp;2 -&amp;gt; 380 kV ABV-GRA3
20231123 | 1830 | November | 7807 | 7662 | 2149 | 216 | -2735 | -2735 | -2590 | Critical Branch | Validation phase | 145 | 0 | IT | 7472 | N-2 380 kV ABV-GRA1&amp;amp;2 -&amp;gt; 380 kV ABV-GRA3
20231123 | 1930 | November | 7807 | 7662 | 2149 | 216 | -2735 | -2735 | -2590 | Critical Branch | Validation phase | 145 | 0 | IT | 7472 | N-2 380 kV ABV-GRA1&amp;amp;2 -&amp;gt; 380 kV ABV-GRA3
20231123 | 2030 | November | 7807 | 7662 | 2149 | 216 | -2735 | -2735 | -2590 | Critical Branch | Validation phase | 145 | 0 | IT | 7472 | N-2 380 kV ABV-GRA1&amp;amp;2 -&amp;gt; 380 kV ABV-GRA3
20231124 | 1730 | November | 8689 | 7489 | 2594 | 190 | -3008 | -3008 | -1808 | Critical Branch | Validation phase | 1200 | 0 | CH | 7299 | Same value as the two other hours
20231125 | 1230 | November | 8439 | 7726 | 2731 | 205 | 384 | 368 | 714 | Minimum Margin | Validation phase | 713 | 698 | FR | 2731 | Bilateral - Echec du calcul reprise NTC de 11h30 | AT | 223 | Reduction because NTC over thermal limit on border | IT | 7610 | Safe Value
20231125 | 1330 | November | 8439 | 7726 | 2731 | 205 | 384 | 368 | 714 | Minimum Margin | Validation phase | 713 | 698 | FR | 2731 | Bilateral - Echec du calcul reprise NTC de 11h30 | AT | 223 | Reduction because NTC over thermal limit on border | IT | 7610 | Safe Value
20231125 | 1430 | November | 8439 | 7726 | 2731 | 205 | 384 | 368 | 714 | Minimum Margin | Validation phase | 713 | 698 | FR | 2731 | Bilateral - Echec du calcul reprise NTC de 11h30 | AT | 223 | Reduction because NTC over thermal limit on border | IT | 7610 | Safe Value
20231125 | 1730 | November | 8100 | 7800 | 2710 | 198 | -3511 | -3511 | -3211 | TTC Selection - LTTC | Validation phase | 300 | 0 | IT | 7610 | Safe Value
20231125 | 1830 | November | 8189 | 7800 | 2710 | 198 | -986 | -986 | -597 | Critical Branch | Validation phase | 389 | 0 | IT | 7610 | Safe Value
20231125 | 1930 | November | 8189 | 7800 | 2710 | 198 | -986 | -986 | -597 | Critical Branch | Validation phase | 389 | 0 | IT | 7610 | Safe Value
20231125 | 2030 | November | 8189 | 7800 | 2710 | 198 | -986 | -986 | -597 | Critical Branch | Validation phase | 389 | 0 | IT | 7610 | Safe Value
20231125 | 2130 | November | 8421 | 7800 | 2710 | 198 | -1059 | -1059 | -438 | Critical Branch | Validation phase | 621 | 0 | IT | 7610 | Safe Value
20231125 | 2230 | November | 8421 | 7800 | 2710 | 198 | -1059 | -1059 | -438 | Critical Branch | Validation phase | 621 | 0 | IT | 7610 | Safe Value
20231126 | 0730 | November | 8661 | 8461 | 3019 | 216 | -3451 | -3451 | -3251 | Critical Branch | Validation phase | 200 | 0 | IT | 8271 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo-Musignano, C: N-1 Soazza-Bulciago
20231126 | 0930 | November | 8799 | 8399 | 2995 | 215 | -1851 | -1851 | -1451 | Critical Branch | Validation phase | 400 | 0 | IT | 8209 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo-Musignano, C: N-1 Soazza-Bulciago
20231126 | 1030 | November | 8799 | 8399 | 2995 | 215 | -1851 | -1851 | -1451 | Critical Branch | Validation phase | 400 | 0 | IT | 8209 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo-Musignano, C: N-1 Soazza-Bulciago
20231126 | 1130 | November | 8799 | 8399 | 2995 | 215 | -1851 | -1851 | -1451 | Critical Branch | Validation phase | 400 | 0 | IT | 8209 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo-Musignano, C: N-1 Soazza-Bulciago
20231126 | 1230 | November | 8800 | 8400 | 2995 | 215 | -3643 | -3643 | -3243 | Critical Branch | Validation phase | 400 | 0 | IT | 8210 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo-Musignano, C: N-1 Soazza-Bulciago
20231126 | 1330 | November | 8800 | 8400 | 2995 | 215 | -3643 | -3643 | -3243 | Critical Branch | Validation phase | 400 | 0 | IT | 8210 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo-Musignano, C: N-1 Soazza-Bulciago
20231126 | 1430 | November | 8800 | 8400 | 2995 | 215 | -3643 | -3643 | -3243 | Critical Branch | Validation phase | 400 | 0 | IT | 8210 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo-Musignano, C: N-1 Soazza-Bulciago
20231126 | 1530 | November | 8732 | 8432 | 3008 | 216 | -4781 | -4781 | -4481 | Critical Branch | Validation phase | 300 | 0 | IT | 8242 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo-Musignano, C: N-1 Soazza-Bulciago
20231126 | 1630 | November | 8732 | 8432 | 3008 | 216 | -4781 | -4781 | -4481 | Critical Branch | Validation phase | 300 | 0 | IT | 8242 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo-Musignano, C: N-1 Soazza-Bulciago
20231126 | 1730 | November | 9032 | 8432 | 2902 | 208 | -5059 | -5059 | -4459 | Critical Branch | Validation phase | 600 | 0 | IT | 8242 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo-Musignano, C: N-1 Soazza-Bulciago
20231126 | 1830 | November | 8899 | 8399 | 2890 | 207 | -1797 | -1797 | -1297 | Critical Branch | Validation phase | 500 | 0 | IT | 8209 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo-Musignano, C: N-1 Soazza-Bulciago
20231126 | 1930 | November | 8899 | 8399 | 2890 | 207 | -1797 | -1797 | -1297 | Critical Branch | Validation phase | 500 | 0 | IT | 8209 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo-Musignano, C: N-1 Soazza-Bulciago
20231126 | 2030 | November | 8899 | 8399 | 2890 | 207 | -1797 | -1797 | -1297 | Critical Branch | Validation phase | 500 | 0 | IT | 8209 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo-Musignano, C: N-1 Soazza-Bulciago
20231126 | 2130 | November | 9009 | 8409 | 2894 | 208 | -1564 | -1564 | -964 | Critical Branch | Validation phase | 600 | 0 | IT | 8219 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo-Musignano, C: N-1 Soazza-Bulciago
20231126 | 2230 | November | 9009 | 8409 | 2894 | 208 | -1564 | -1564 | -964 | Critical Branch | Validation phase | 600 | 0 | IT | 8219 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo-Musignano, C: N-1 Soazza-Bulciago
20231127 | 0030 | November | 7946 | 7540 | 2500 | 208 | -1553 | -1553 | -1189 | Critical Branch | Critical Branch | 406 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT | AT | 225 | Reduction because NTC over thermal limit on border
20231127 | 0130 | November | 7946 | 7540 | 2500 | 208 | -1553 | -1553 | -1189 | Critical Branch | Critical Branch | 406 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT | AT | 225 | Reduction because NTC over thermal limit on border
20231127 | 0230 | November | 7946 | 7540 | 2500 | 208 | -1553 | -1553 | -1189 | Critical Branch | Critical Branch | 406 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT | AT | 225 | Reduction because NTC over thermal limit on border
20231127 | 0330 | November | 7911 | 7518 | 2500 | 207 | -1150 | -1150 | -797 | Critical Branch | Critical Branch | 393 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT | AT | 225 | Reduction because NTC over thermal limit on border
20231127 | 0430 | November | 7911 | 7518 | 2500 | 207 | -1150 | -1150 | -797 | Critical Branch | Critical Branch | 393 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT | AT | 225 | Reduction because NTC over thermal limit on border
20231127 | 0530 | November | 7911 | 7518 | 2500 | 207 | -1150 | -1150 | -797 | Critical Branch | Critical Branch | 393 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT | AT | 225 | Reduction because NTC over thermal limit on border
20231127 | 0630 | November | 7911 | 7518 | 2500 | 207 | -1150 | -1150 | -797 | Critical Branch | Critical Branch | 393 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT | AT | 225 | Reduction because NTC over thermal limit on border
20231127 | 0730 | November | 8028 | 7442 | 2500 | 225 | -1262 | -1262 | -744 | Critical Branch | Critical Branch | 586 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT | AT | 240 | Reduction because NTC over thermal limit on border
20231127 | 0830 | November | 8028 | 7442 | 2500 | 225 | -1262 | -1262 | -744 | Critical Branch | Critical Branch | 586 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT | AT | 240 | Reduction because NTC over thermal limit on border
20231127 | 0930 | November | 7874 | 7351 | 2500 | 221 | -1219 | -1219 | -759 | Critical Branch | Critical Branch | 523 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT | AT | 240 | Reduction because NTC over thermal limit on border
20231127 | 1030 | November | 7874 | 7351 | 2500 | 221 | -1219 | -1219 | -759 | Critical Branch | Critical Branch | 523 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT | AT | 240 | Reduction because NTC over thermal limit on border
20231127 | 1130 | November | 7874 | 7351 | 2500 | 221 | -1219 | -1219 | -759 | Critical Branch | Critical Branch | 523 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT | AT | 240 | Reduction because NTC over thermal limit on border
20231127 | 1230 | November | 7883 | 7357 | 2500 | 221 | -791 | -791 | -336 | Critical Branch | Critical Branch | 526 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT | AT | 240 | Reduction because NTC over thermal limit on border
20231127 | 1330 | November | 7883 | 7357 | 2500 | 221 | -791 | -791 | -336 | Critical Branch | Critical Branch | 526 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT | AT | 240 | Reduction because NTC over thermal limit on border
20231127 | 1430 | November | 7883 | 7357 | 2500 | 221 | -791 | -791 | -336 | Critical Branch | Critical Branch | 526 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT | AT | 240 | Reduction because NTC over thermal limit on border
20231127 | 1530 | November | 8507 | 7607 | 2500 | 234 | -3600 | -3600 | -2484 | Critical Branch | Validation phase | 900 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT | AT | 240 | Reduction because NTC over thermal limit on border | IT | 8117 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo-Musignano, C: N-1 Soazza-Bulciago
20231127 | 1630 | November | 8507 | 7607 | 2500 | 234 | -3600 | -3600 | -2484 | Critical Branch | Validation phase | 900 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT | AT | 240 | Reduction because NTC over thermal limit on border | IT | 8117 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo-Musignano, C: N-1 Soazza-Bulciago
20231127 | 1730 | November | 8807 | 7722 | 2500 | 225 | -3858 | -3858 | -2589 | Critical Branch | Validation phase | 1085 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT | AT | 240 | Reduction because NTC over thermal limit on border | IT | 8117 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo-Musignano, C: N-1 Soazza-Bulciago
20231127 | 1830 | November | 9251 | 7749 | 2500 | 227 | -2399 | -2399 | -935 | Critical Branch | Validation phase | 1502 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT | AT | 240 | Reduction because NTC over thermal limit on border | IT | 8161 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo-Musignano, C: N-1 Soazza-Bulciago
20231127 | 1930 | November | 9251 | 7749 | 2500 | 227 | -2399 | -2399 | -935 | Critical Branch | Validation phase | 1502 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT | AT | 240 | Reduction because NTC over thermal limit on border | IT | 8161 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo-Musignano, C: N-1 Soazza-Bulciago
20231127 | 2030 | November | 9251 | 7749 | 2500 | 227 | -2399 | -2399 | -935 | Critical Branch | Validation phase | 1502 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT | AT | 240 | Reduction because NTC over thermal limit on border | IT | 8161 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo-Musignano, C: N-1 Soazza-Bulciago
20231127 | 2130 | November | 8623 | 7732 | 2500 | 226 | -1961 | -1961 | -1135 | Critical Branch | Validation phase | 891 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT | AT | 240 | Reduction because NTC over thermal limit on border | IT | 8133 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo-Musignano, C: N-1 Soazza-Bulciago
20231127 | 2230 | November | 8623 | 7732 | 2500 | 226 | -1961 | -1961 | -1135 | Critical Branch | Validation phase | 891 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT | AT | 240 | Reduction because NTC over thermal limit on border | IT | 8133 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo-Musignano, C: N-1 Soazza-Bulciago
20231127 | 2330 | November | 8349 | 7786 | 2500 | 220 | -1732 | -1732 | -1232 | Critical Branch | Critical Branch | 563 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT | AT | 225 | Reduction because NTC over thermal limit on border
20231128 | 0030 | November | 7390 | 7201 | 2500 | 193 | -9315 | -9315 | -9114 | TTC Selection - LTTC | TTC Selection - LTTC | 189 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT
20231128 | 0130 | November | 7390 | 7201 | 2500 | 193 | -9315 | -9315 | -9114 | TTC Selection - LTTC | TTC Selection - LTTC | 189 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT
20231128 | 0230 | November | 7390 | 7201 | 2500 | 193 | -9315 | -9315 | -9114 | TTC Selection - LTTC | TTC Selection - LTTC | 189 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT
20231128 | 0330 | November | 8256 | 7729 | 2500 | 217 | -7782 | -7782 | -7254 | Critical Branch | Critical Branch | 527 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT
20231128 | 0430 | November | 8256 | 7729 | 2500 | 217 | -7782 | -7782 | -7254 | Critical Branch | Critical Branch | 527 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT
20231128 | 0530 | November | 8256 | 7729 | 2500 | 217 | -7782 | -7782 | -7254 | Critical Branch | Critical Branch | 527 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT
20231128 | 0630 | November | 8256 | 7729 | 2500 | 217 | -7782 | -7782 | -7254 | Critical Branch | Critical Branch | 527 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT
20231128 | 0730 | November | 9089 | 7900 | 2500 | 223 | -4632 | -4632 | -3470 | Critical Branch | Validation phase | 1189 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT |  |  |  | CH | 8268 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231128 | 0830 | November | 9089 | 7900 | 2500 | 223 | -4632 | -4632 | -3470 | Critical Branch | Validation phase | 1189 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT |  |  |  | CH | 8268 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231128 | 0930 | November | 7880 | 7545 | 2500 | 207 | 80 | 80 | 504 | Minimum Margin | Minimum Margin | 335 | 504 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT
20231128 | 1030 | November | 7880 | 7545 | 2500 | 207 | 80 | 80 | 504 | Minimum Margin | Minimum Margin | 335 | 504 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT
20231128 | 1130 | November | 7880 | 7545 | 2500 | 207 | 80 | 80 | 504 | Minimum Margin | Minimum Margin | 335 | 504 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT
20231128 | 1230 | November | 7933 | 7577 | 2500 | 209 | -1535 | -1535 | -1050 | Critical Branch | Critical Branch | 356 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT
20231128 | 1330 | November | 7933 | 7577 | 2500 | 209 | -1535 | -1535 | -1050 | Critical Branch | Critical Branch | 356 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT
20231128 | 1430 | November | 7933 | 7577 | 2500 | 209 | -1535 | -1535 | -1050 | Critical Branch | Critical Branch | 356 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT
20231128 | 1530 | November | 8187 | 7734 | 2500 | 216 | -2177 | -2177 | -1614 | Critical Branch | Critical Branch | 453 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT
20231128 | 1630 | November | 8187 | 7734 | 2500 | 216 | -2177 | -2177 | -1614 | Critical Branch | Critical Branch | 453 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT
20231128 | 1730 | November | 8487 | 8022 | 2500 | 217 | -2459 | -2459 | -1883 | Critical Branch | Critical Branch | 465 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT
20231128 | 1830 | November | 9283 | 8004 | 2500 | 216 | -2729 | -2729 | -1494 | Critical Branch | Validation phase | 1279 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT |  |  |  | CH | 8268 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231128 | 1930 | November | 9283 | 8004 | 2500 | 216 | -2729 | -2729 | -1494 | Critical Branch | Validation phase | 1279 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT |  |  |  | CH | 8268 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231128 | 2030 | November | 9283 | 8004 | 2500 | 216 | -2729 | -2729 | -1494 | Critical Branch | Validation phase | 1279 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT |  |  |  | CH | 8268 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231128 | 2130 | November | 8694 | 8004 | 2500 | 216 | -1836 | -1836 | -1200 | Critical Branch | Validation phase | 690 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT |  |  |  | CH | 8268 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231128 | 2230 | November | 8694 | 8004 | 2500 | 216 | -1836 | -1836 | -1200 | Critical Branch | Validation phase | 690 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT |  |  |  | CH | 8268 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231128 | 2330 | November | 7884 | 7502 | 2500 | 207 | -1005 | -1005 | -670 | Critical Branch | Critical Branch | 382 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT
20231129 | 0030 | November | 8657 | 7973 | 2500 | 228 | -1545 | -1545 | -958 | Critical Branch | Critical Branch | 684 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT 2
20231129 | 0130 | November | 8657 | 7973 | 2500 | 228 | -1545 | -1545 | -958 | Critical Branch | Critical Branch | 684 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT 2
20231129 | 0230 | November | 8657 | 7973 | 2500 | 228 | -1545 | -1545 | -958 | Critical Branch | Critical Branch | 684 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT 2
20231129 | 0330 | November | 8560 | 7914 | 2500 | 226 | -1219 | -1219 | -655 | Critical Branch | Critical Branch | 646 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT 2
20231129 | 0430 | November | 8560 | 7914 | 2500 | 226 | -1219 | -1219 | -655 | Critical Branch | Critical Branch | 646 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT 2
20231129 | 0530 | November | 8560 | 7914 | 2500 | 226 | -1219 | -1219 | -655 | Critical Branch | Critical Branch | 646 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT 2
20231129 | 0630 | November | 8560 | 7914 | 2500 | 226 | -1219 | -1219 | -655 | Critical Branch | Critical Branch | 646 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT 2
20231129 | 0730 | November | 8471 | 7908 | 2500 | 224 | -2530 | -2530 | -1969 | Critical Branch | Critical Branch | 563 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT 2
20231129 | 0830 | November | 8471 | 7908 | 2500 | 224 | -2530 | -2530 | -1969 | Critical Branch | Critical Branch | 563 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT 2
20231129 | 0930 | November | 8788 | 8104 | 2500 | 233 | -2427 | -2427 | -1789 | Critical Branch | Critical Branch | 684 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT 2
20231129 | 1030 | November | 8788 | 8104 | 2500 | 233 | -2427 | -2427 | -1789 | Critical Branch | Critical Branch | 684 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT 2
20231129 | 1130 | November | 8788 | 8104 | 2500 | 233 | -2427 | -2427 | -1789 | Critical Branch | Critical Branch | 684 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT 2
20231129 | 1230 | November | 8413 | 7873 | 2500 | 222 | -1026 | -1026 | -318 | Critical Branch | Critical Branch | 540 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT 2
20231129 | 1330 | November | 8413 | 7873 | 2500 | 222 | -1026 | -1026 | -318 | Critical Branch | Critical Branch | 540 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT 2
20231129 | 1430 | November | 8413 | 7873 | 2500 | 222 | -1026 | -1026 | -318 | Critical Branch | Critical Branch | 540 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT 2
20231129 | 1530 | November | 8134 | 7701 | 2500 | 214 | -1081 | -1081 | -694 | Critical Branch | Critical Branch | 433 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT 2
20231129 | 1630 | November | 8134 | 7701 | 2500 | 214 | -1081 | -1081 | -694 | Critical Branch | Critical Branch | 433 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT 2
20231129 | 1730 | November | 8434 | 7989 | 2500 | 215 | -1412 | -1412 | -1014 | Critical Branch | Critical Branch | 445 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT 2
20231129 | 1830 | November | 8100 | 7779 | 2500 | 206 | -6805 | -6805 | -6490 | TTC Selection - LTTC | TTC Selection - LTTC | 321 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT 2
20231129 | 1930 | November | 8100 | 7779 | 2500 | 206 | -6805 | -6805 | -6490 | TTC Selection - LTTC | TTC Selection - LTTC | 321 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT 2
20231129 | 2030 | November | 8100 | 7779 | 2500 | 206 | -6805 | -6805 | -6490 | TTC Selection - LTTC | TTC Selection - LTTC | 321 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT 2
20231129 | 2130 | November | 8100 | 7779 | 2500 | 206 | -8500 | -8500 | -8172 | TTC Selection - LTTC | TTC Selection - LTTC | 321 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT 2
20231129 | 2230 | November | 8100 | 7779 | 2500 | 206 | -8500 | -8500 | -8172 | TTC Selection - LTTC | TTC Selection - LTTC | 321 | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT 2
20231130 | 0030 | November | 8540 | 5807 | 2071 | 149 |  |  |  | Scheduled TTC | Validation phase | 2733 | 0 | IT | 5617 | Safe Value
20231130 | 0130 | November | 8540 | 5807 | 2071 | 149 |  |  |  | Scheduled TTC | Validation phase | 2733 | 0 | IT | 5617 | Safe Value
20231130 | 0230 | November | 8540 | 5807 | 2071 | 149 |  |  |  | Scheduled TTC | Validation phase | 2733 | 0 | IT | 5617 | Safe Value
20231130 | 0330 | November | 8540 | 6148 | 2204 | 158 |  |  |  | Scheduled TTC | Validation phase | 2392 | 0 | IT | 5958 | CO Value
20231130 | 0430 | November | 8540 | 6148 | 2204 | 158 |  |  |  | Scheduled TTC | Validation phase | 2392 | 0 | IT | 5958 | CO Value
20231130 | 0530 | November | 8540 | 6148 | 2204 | 158 |  |  |  | Scheduled TTC | Validation phase | 2392 | 0 | IT | 5958 | CO Value
20231130 | 0630 | November | 8540 | 6148 | 2204 | 158 |  |  |  | Scheduled TTC | Validation phase | 2392 | 0 | IT | 5958 | CO Value
20231130 | 0730 | November | 9350 | 5865 | 1991 | 145 |  |  |  | Scheduled TTC | Validation phase | 3485 | 0 | IT | 5675 | CO Value
20231130 | 0830 | November | 9350 | 5865 | 1991 | 145 |  |  |  | Scheduled TTC | Validation phase | 3485 | 0 | IT | 5675 | CO Value
20231130 | 0930 | November | 9350 | 7365 | 2349 | 195 |  |  |  | Scheduled TTC | Smoothing ramp | 1985 | 0 | Smoothing
20231130 | 1030 | November | 9350 | 7806 | 2500 | 207 |  |  |  | Scheduled TTC | Validation phase | 1544 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border | IT | 7953 | CO Value
20231130 | 1130 | November | 9350 | 7806 | 2500 | 207 |  |  |  | Scheduled TTC | Validation phase | 1544 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border | IT | 7953 | CO Value
20231130 | 1230 | November | 9350 | 7560 | 2500 | 197 |  |  |  | Scheduled TTC | Validation phase | 1790 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border | IT | 7562 | CO Value
20231130 | 1330 | November | 9350 | 7560 | 2500 | 197 |  |  |  | Scheduled TTC | Validation phase | 1790 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border | IT | 7562 | CO Value
20231130 | 1430 | November | 9350 | 7560 | 2500 | 197 |  |  |  | Scheduled TTC | Validation phase | 1790 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border | IT | 7562 | CO Value
20231130 | 1530 | November | 9350 | 7779 | 2500 | 206 |  |  |  | Scheduled TTC | Validation phase | 1571 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border | IT | 7910 | LTTC
20231130 | 1630 | November | 9350 | 7779 | 2500 | 206 |  |  |  | Scheduled TTC | Validation phase | 1571 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border | IT | 7910 | LTTC
20231130 | 1730 | November | 9350 | 7779 | 2500 | 206 |  |  |  | Scheduled TTC | Validation phase | 1571 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border | IT | 7910 | LTTC
20231130 | 1830 | November | 9350 | 7619 | 2500 | 199 |  |  |  | Scheduled TTC | Validation phase | 1731 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border | IT | 7656 | CO Value
20231130 | 1930 | November | 9350 | 7619 | 2500 | 199 |  |  |  | Scheduled TTC | Validation phase | 1731 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border | IT | 7656 | CO Value
20231130 | 2030 | November | 9350 | 7619 | 2500 | 199 |  |  |  | Scheduled TTC | Validation phase | 1731 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border | IT | 7656 | CO Value
20231130 | 2130 | November | 9350 | 6716 | 2307 | 169 |  |  |  | Scheduled TTC | Validation phase | 2634 | 0 | IT | 6526 | CO value
20231130 | 2230 | November | 9350 | 6716 | 2307 | 169 |  |  |  | Scheduled TTC | Validation phase | 2634 | 0 | IT | 6526 | CO value
20231130 | 2330 | November | 8540 | 6716 | 2426 | 174 |  |  |  | Scheduled TTC | Validation phase | 1824 | 0 | IT | 6526 | CO value
20231201 | 0030 | December | 7390 | 7201 | 2500 | 193 | -5972 | -5972 | -5786 | TTC Selection - LTTC | TTC Selection - LTTC | 189 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 193 | Reduction because NTC over thermal limit on border
20231201 | 0130 | December | 7390 | 7201 | 2500 | 193 | -5972 | -5972 | -5786 | TTC Selection - LTTC | TTC Selection - LTTC | 189 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 193 | Reduction because NTC over thermal limit on border
20231201 | 0230 | December | 7390 | 7201 | 2500 | 193 | -5972 | -5972 | -5786 | TTC Selection - LTTC | TTC Selection - LTTC | 189 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 225 | Reduction because NTC over thermal limit on border
20231201 | 0330 | December | 8594 | 7506 | 2500 | 207 | -5965 | -5965 | -4894 | Critical Branch | Validation phase | 1088 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 225 | Reduction because NTC over thermal limit on border | IT | 7700 | ABV-GRA 1/2 on ABV-GRA 3
20231201 | 0430 | December | 8594 | 7506 | 2500 | 207 | -5965 | -5965 | -4894 | Critical Branch | Validation phase | 1088 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 225 | Reduction because NTC over thermal limit on border | IT | 7700 | ABV-GRA 1/2 on ABV-GRA 3
20231201 | 0530 | December | 8594 | 7506 | 2500 | 207 | -5965 | -5965 | -4894 | Critical Branch | Validation phase | 1088 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 225 | Reduction because NTC over thermal limit on border | IT | 7700 | ABV-GRA 1/2 on ABV-GRA 3
20231201 | 0630 | December | 8594 | 7506 | 2500 | 207 | -5965 | -5965 | -4894 | Critical Branch | Validation phase | 1088 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 225 | Reduction because NTC over thermal limit on border | IT | 7700 | ABV-GRA 1/2 on ABV-GRA 3
20231201 | 0730 | December | 8100 | 7779 | 2500 | 206 | -4075 | -4075 | -3781 | TTC Selection - LTTC | TTC Selection - LTTC | 321 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231201 | 0830 | December | 8100 | 7779 | 2500 | 206 | -4075 | -4075 | -3781 | TTC Selection - LTTC | TTC Selection - LTTC | 321 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231201 | 0930 | December | 8213 | 7483 | 2500 | 193 | -3568 | -3568 | -2844 | Critical Branch | Validation phase | 730 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border | CH | 7439 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-1 AVISE-RIDDES
20231201 | 1030 | December | 8213 | 7483 | 2500 | 193 | -3568 | -3568 | -2844 | Critical Branch | Validation phase | 730 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border | CH | 7439 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-1 AVISE-RIDDES
20231201 | 1130 | December | 8213 | 7483 | 2500 | 193 | -3568 | -3568 | -2844 | Critical Branch | Validation phase | 730 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border | CH | 7439 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-1 AVISE-RIDDES
20231201 | 1230 | December | 8511 | 7773 | 2500 | 206 | -983 | -983 | -100 | Critical Branch | Validation phase | 738 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border | IT | 7900 | ABV-GRA 1/2 on ABV-GRA 3
20231201 | 1330 | December | 8511 | 7773 | 2500 | 206 | -983 | -983 | -100 | Critical Branch | Validation phase | 738 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border | IT | 7900 | ABV-GRA 1/2 on ABV-GRA 3
20231201 | 1430 | December | 8511 | 7773 | 2500 | 206 | -983 | -983 | -100 | Critical Branch | Validation phase | 738 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border | IT | 7900 | ABV-GRA 1/2 on ABV-GRA 3
20231201 | 1530 | December | 8100 | 7551 | 2500 | 196 | -3440 | -3440 | -2909 | TTC Selection - LTTC | Validation phase | 549 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border | CH | 7548 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-1 AVISE-RIDDES
20231201 | 1630 | December | 8100 | 7551 | 2500 | 196 | -3440 | -3440 | -2909 | TTC Selection - LTTC | Validation phase | 549 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border | CH | 7548 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-1 AVISE-RIDDES
20231201 | 1730 | December | 8100 | 7551 | 2500 | 196 | -3440 | -3440 | -2909 | TTC Selection - LTTC | Validation phase | 549 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border | CH | 7548 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-1 AVISE-RIDDES
20231201 | 1830 | December | 8100 | 7779 | 2500 | 206 | -5979 | -5979 | -5670 | TTC Selection - LTTC | TTC Selection - LTTC | 321 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231201 | 1930 | December | 8100 | 7779 | 2500 | 206 | -5979 | -5979 | -5670 | TTC Selection - LTTC | TTC Selection - LTTC | 321 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231201 | 2030 | December | 8100 | 7779 | 2500 | 206 | -5979 | -5979 | -5670 | TTC Selection - LTTC | TTC Selection - LTTC | 321 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231201 | 2130 | December | 8100 | 7779 | 2500 | 206 | -7427 | -7427 | -7107 | TTC Selection - LTTC | TTC Selection - LTTC | 321 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231201 | 2230 | December | 8100 | 7779 | 2500 | 206 | -7427 | -7427 | -7107 | TTC Selection - LTTC | TTC Selection - LTTC | 321 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231202 | 0030 | December | 8492 | 7873 | 2500 | 224 | -2522 | -2522 | -1976 | Critical Branch | Critical Branch | 619 | 0 | FR | 2500 | Bilateral - RDCR CREYS-GENISSIAT 1 | AT | 224 | Reduction because NTC over thermal limit on border
20231202 | 0230 | December | 8492 | 7873 | 2500 | 224 | -2522 | -2522 | -1976 | Critical Branch | Critical Branch | 619 | 0 | FR | 2500 | Bilateral - RDCR CREYS-GENISSIAT 1 | AT | 225 | Reduction because NTC over thermal limit on border
20231202 | 0330 | December | 7390 | 7201 | 2500 | 193 | -2795 | -2795 | -2624 | TTC Selection - LTTC | TTC Selection - LTTC | 189 | 0 | FR | 2500 | Bilateral - RDCR CREYS-GENISSIAT 1 | AT | 225 | Reduction because NTC over thermal limit on border
20231202 | 0430 | December | 7390 | 7201 | 2500 | 193 | -2795 | -2795 | -2624 | TTC Selection - LTTC | TTC Selection - LTTC | 189 | 0 | FR | 2500 | Bilateral - RDCR CREYS-GENISSIAT 1 | AT | 225 | Reduction because NTC over thermal limit on border
20231202 | 0530 | December | 7390 | 7201 | 2500 | 193 | -2795 | -2795 | -2624 | TTC Selection - LTTC | TTC Selection - LTTC | 189 | 0 | FR | 2500 | Bilateral - RDCR CREYS-GENISSIAT 1 | AT | 225 | Reduction because NTC over thermal limit on border
20231202 | 0630 | December | 7390 | 7201 | 2500 | 193 | -2795 | -2795 | -2624 | TTC Selection - LTTC | TTC Selection - LTTC | 189 | 0 | FR | 2500 | Bilateral - RDCR CREYS-GENISSIAT 1 | AT | 225 | Reduction because NTC over thermal limit on border
20231202 | 0730 | December | 8100 | 7779 | 2500 | 206 | -4984 | -4984 | -4682 | TTC Selection - LTTC | TTC Selection - LTTC | 321 | 0 | FR | 2500 | Bilateral - RDCR CREYS-GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231202 | 0930 | December | 7200 | 6932 | 2500 | 202 | -4309 | -4309 | -4057 | TTC Selection - LTTC | TTC Selection - LTTC | 268 | 0 | FR | 2500 | Bilateral - RDCR CREYS-GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231202 | 1030 | December | 7200 | 6932 | 2500 | 202 | -4309 | -4309 | -4057 | TTC Selection - LTTC | TTC Selection - LTTC | 268 | 0 | FR | 2500 | Bilateral - RDCR CREYS-GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231202 | 1130 | December | 7200 | 6932 | 2500 | 202 | -4309 | -4309 | -4057 | TTC Selection - LTTC | TTC Selection - LTTC | 268 | 0 | FR | 2500 | Bilateral - RDCR CREYS-GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231202 | 1230 | December | 7200 | 6932 | 2500 | 202 | -3576 | -3576 | -3330 | TTC Selection - LTTC | TTC Selection - LTTC | 268 | 0 | FR | 2500 | Bilateral - RDCR CREYS-GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231202 | 1330 | December | 7200 | 6932 | 2500 | 202 | -3576 | -3576 | -3330 | TTC Selection - LTTC | TTC Selection - LTTC | 268 | 0 | FR | 2500 | Bilateral - RDCR CREYS-GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231202 | 1430 | December | 7200 | 6932 | 2500 | 202 | -3576 | -3576 | -3330 | TTC Selection - LTTC | TTC Selection - LTTC | 268 | 0 | FR | 2500 | Bilateral - RDCR CREYS-GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231202 | 1530 | December | 7570 | 7149 | 2500 | 213 | 1052 | 370 | 1468 | Minimum Margin | Minimum Margin | 421 | 786 | FR | 2500 | Bilateral - RDCR CREYS-GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231202 | 1630 | December | 7570 | 7149 | 2500 | 213 | 1052 | 370 | 1468 | Minimum Margin | Minimum Margin | 421 | 786 | FR | 2500 | Bilateral - RDCR CREYS-GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231202 | 1730 | December | 7570 | 7149 | 2500 | 213 | 1052 | 370 | 1468 | Minimum Margin | Minimum Margin | 421 | 786 | FR | 2500 | Bilateral - RDCR CREYS-GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231202 | 1830 | December | 8100 | 7779 | 2500 | 206 | -7239 | -7239 | -6921 | TTC Selection - LTTC | TTC Selection - LTTC | 321 | 0 | FR | 2500 | Bilateral - RDCR CREYS-GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231202 | 1930 | December | 8100 | 7779 | 2500 | 206 | -7239 | -7239 | -6921 | TTC Selection - LTTC | TTC Selection - LTTC | 321 | 0 | FR | 2500 | Bilateral - RDCR CREYS-GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231202 | 2030 | December | 8100 | 7779 | 2500 | 206 | -7239 | -7239 | -6921 | TTC Selection - LTTC | TTC Selection - LTTC | 321 | 0 | FR | 2500 | Bilateral - RDCR CREYS-GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231202 | 2130 | December | 8100 | 7779 | 2500 | 206 | -9417 | -9417 | -9083 | TTC Selection - LTTC | TTC Selection - LTTC | 321 | 0 | FR | 2500 | Bilateral - RDCR CREYS-GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231202 | 2230 | December | 8100 | 7779 | 2500 | 206 | -9417 | -9417 | -9083 | TTC Selection - LTTC | TTC Selection - LTTC | 321 | 0 | FR | 2500 | Bilateral - RDCR CREYS-GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231204 | 0030 | December | 7390 | 7201 | 2500 | 193 | -9736 | -9736 | -9534 | TTC Selection - LTTC | TTC Selection - LTTC | 189 | 0 | FR | 2500 | Bilateral - retrait CREYS GENISSIAT 1 | AT | 193 | Reduction because NTC over thermal limit on border
20231204 | 0130 | December | 7390 | 7201 | 2500 | 193 | -9736 | -9736 | -9534 | TTC Selection - LTTC | TTC Selection - LTTC | 189 | 0 | FR | 2500 | Bilateral - retrait CREYS GENISSIAT 1 | AT | 193 | Reduction because NTC over thermal limit on border
20231204 | 0230 | December | 7390 | 7201 | 2500 | 193 | -9736 | -9736 | -9534 | TTC Selection - LTTC | TTC Selection - LTTC | 189 | 0 | FR | 2500 | Bilateral - retrait CREYS GENISSIAT 1 | AT | 225 | Reduction because NTC over thermal limit on border
20231204 | 0330 | December | 7390 | 7201 | 2500 | 193 | -9337 | -9337 | -9136 | TTC Selection - LTTC | TTC Selection - LTTC | 189 | 0 | FR | 2500 | Bilateral - retrait CREYS GENISSIAT 1 | AT | 225 | Reduction because NTC over thermal limit on border
20231204 | 0430 | December | 7390 | 7201 | 2500 | 193 | -9337 | -9337 | -9136 | TTC Selection - LTTC | TTC Selection - LTTC | 189 | 0 | FR | 2500 | Bilateral - retrait CREYS GENISSIAT 1 | AT | 225 | Reduction because NTC over thermal limit on border
20231204 | 0530 | December | 7390 | 7201 | 2500 | 193 | -9337 | -9337 | -9136 | TTC Selection - LTTC | TTC Selection - LTTC | 189 | 0 | FR | 2500 | Bilateral - retrait CREYS GENISSIAT 1 | AT | 225 | Reduction because NTC over thermal limit on border
20231204 | 0630 | December | 7390 | 7201 | 2500 | 193 | -9337 | -9337 | -9136 | TTC Selection - LTTC | TTC Selection - LTTC | 189 | 0 | FR | 2500 | Bilateral - retrait CREYS GENISSIAT 1 | AT | 225 | Reduction because NTC over thermal limit on border
20231204 | 0730 | December | 7623 | 7166 | 2500 | 216 | -3568 | -3568 | -3136 | Critical Branch | Critical Branch | 457 | 0 | FR | 2500 | Bilateral - retrait CREYS GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231204 | 0830 | December | 7623 | 7166 | 2500 | 216 | -3568 | -3568 | -3136 | Critical Branch | Critical Branch | 457 | 0 | FR | 2500 | Bilateral - retrait CREYS GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231204 | 0930 | December | 7342 | 7002 | 2500 | 207 | -3243 | -3243 | -2938 | Critical Branch | Critical Branch | 340 | 0 | FR | 2500 | Bilateral - retrait CREYS GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231204 | 1030 | December | 7342 | 7002 | 2500 | 207 | -3243 | -3243 | -2938 | Critical Branch | Critical Branch | 340 | 0 | FR | 2500 | Bilateral - retrait CREYS GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231204 | 1130 | December | 7342 | 7002 | 2500 | 207 | -3243 | -3243 | -2938 | Critical Branch | Critical Branch | 340 | 0 | FR | 2500 | Bilateral - retrait CREYS GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231204 | 1230 | December | 7459 | 7070 | 2500 | 211 | -3145 | -3145 | -2781 | Critical Branch | Critical Branch | 389 | 0 | FR | 2500 | Bilateral - retrait CREYS GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231204 | 1330 | December | 7459 | 7070 | 2500 | 211 | -3145 | -3145 | -2781 | Critical Branch | Critical Branch | 389 | 0 | FR | 2500 | Bilateral - retrait CREYS GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231204 | 1430 | December | 7459 | 7070 | 2500 | 211 | -3145 | -3145 | -2781 | Critical Branch | Critical Branch | 389 | 0 | FR | 2500 | Bilateral - retrait CREYS GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231204 | 1530 | December | 7164 | 6898 | 2500 | 202 | -5342 | -5342 | -5085 | TTC Selection - LTTC | TTC Selection - LTTC | 266 | 0 | FR | 2500 | Bilateral - retrait CREYS GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231204 | 1630 | December | 7164 | 6898 | 2500 | 202 | -5342 | -5342 | -5085 | TTC Selection - LTTC | TTC Selection - LTTC | 266 | 0 | FR | 2500 | Bilateral - retrait CREYS GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231204 | 1730 | December | 7164 | 6898 | 2500 | 202 | -5342 | -5342 | -5085 | TTC Selection - LTTC | TTC Selection - LTTC | 266 | 0 | FR | 2500 | Bilateral - retrait CREYS GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231204 | 1830 | December | 7164 | 6898 | 2500 | 202 | -5288 | -5288 | -5033 | TTC Selection - LTTC | TTC Selection - LTTC | 266 | 0 | FR | 2500 | Bilateral - retrait CREYS GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231204 | 1930 | December | 7164 | 6898 | 2500 | 202 | -5288 | -5288 | -5033 | TTC Selection - LTTC | TTC Selection - LTTC | 266 | 0 | FR | 2500 | Bilateral - retrait CREYS GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231204 | 2030 | December | 7164 | 6898 | 2500 | 202 | -5288 | -5288 | -5033 | TTC Selection - LTTC | TTC Selection - LTTC | 266 | 0 | FR | 2500 | Bilateral - retrait CREYS GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231204 | 2130 | December | 7164 | 6898 | 2500 | 202 | -8464 | -8464 | -8185 | TTC Selection - LTTC | TTC Selection - LTTC | 266 | 0 | FR | 2500 | Bilateral - retrait CREYS GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231204 | 2230 | December | 7164 | 6898 | 2500 | 202 | -8464 | -8464 | -8185 | TTC Selection - LTTC | TTC Selection - LTTC | 266 | 0 | FR | 2500 | Bilateral - retrait CREYS GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231204 | 2330 | December | 6890 | 6765 | 2500 | 188 | -8242 | -8242 | -8111 | TTC Selection - LTTC | TTC Selection - LTTC | 125 | 0 | FR | 2500 | Bilateral - retrait CREYS GENISSIAT 1 | AT | 225 | Reduction because NTC over thermal limit on border
20231205 | 0030 | December | 7786 | 7293 | 2500 | 215 | -1812 | -1812 | -1390 | Critical Branch | Critical Branch | 493 | 0 | FR | 2500 | Bilateral - Retrait Creys Génissiat 1 | AT | 215 | Reduction because NTC over thermal limit on border
20231205 | 0130 | December | 7786 | 7293 | 2500 | 215 | -1812 | -1812 | -1390 | Critical Branch | Critical Branch | 493 | 0 | FR | 2500 | Bilateral - Retrait Creys Génissiat 1 | AT | 215 | Reduction because NTC over thermal limit on border
20231205 | 0230 | December | 7786 | 7293 | 2500 | 215 | -1812 | -1812 | -1390 | Critical Branch | Critical Branch | 493 | 0 | FR | 2500 | Bilateral - Retrait Creys Génissiat 1 | AT | 225 | Reduction because NTC over thermal limit on border
20231205 | 0330 | December | 8781 | 7642 | 2500 | 225 | -3057 | -3057 | -1952 | Critical Branch | Validation phase | 1139 | 0 | FR | 2500 | Bilateral - Retrait Creys Génissiat 1 | AT | 225 | Reduction because NTC over thermal limit on border | IT | 8200 | ABV GRA1&2 su ABV GRA3
20231205 | 0430 | December | 8781 | 7642 | 2500 | 225 | -3057 | -3057 | -1952 | Critical Branch | Validation phase | 1139 | 0 | FR | 2500 | Bilateral - Retrait Creys Génissiat 1 | AT | 225 | Reduction because NTC over thermal limit on border | IT | 8200 | ABV GRA1&amp;2 su ABV GRA3
20231205 | 0530 | December | 8781 | 7642 | 2500 | 225 | -3057 | -3057 | -1952 | Critical Branch | Validation phase | 1139 | 0 | FR | 2500 | Bilateral - Retrait Creys Génissiat 1 | AT | 225 | Reduction because NTC over thermal limit on border | IT | 8200 | ABV GRA1&amp;2 su ABV GRA3
20231205 | 0630 | December | 8781 | 7642 | 2500 | 225 | -3057 | -3057 | -1952 | Critical Branch | Validation phase | 1139 | 0 | FR | 2500 | Bilateral - Retrait Creys Génissiat 1 | AT | 225 | Reduction because NTC over thermal limit on border | IT | 8200 | ABV GRA1&amp;2 su ABV GRA3
20231205 | 0730 | December | 7972 | 6923 | 2000 | 223 | -3176 | -3176 | -2247 | Critical Branch | Critical Branch | 1049 | 0 | FR | 2000 | Bilateral - Retrait Creys Génissiat 1 + essai HVDC FR IT | AT | 240 | Reduction because NTC over thermal limit on border
20231205 | 0830 | December | 7972 | 6923 | 2000 | 223 | -3176 | -3176 | -2247 | Critical Branch | Critical Branch | 1049 | 0 | FR | 2000 | Bilateral - Retrait Creys Génissiat 1 + essai HVDC FR IT | AT | 240 | Reduction because NTC over thermal limit on border
20231205 | 0930 | December | 7777 | 6807 | 2000 | 217 | 1320 | 214 | 2661 | Minimum Margin | Minimum Margin | 970 | 1555 | FR | 2000 | Bilateral - Retrait Creys Génissiat 1 + essai HVDC FR IT | AT | 240 | Reduction because NTC over thermal limit on border
20231205 | 1030 | December | 7777 | 6807 | 2000 | 217 | 1320 | 214 | 2661 | Minimum Margin | Minimum Margin | 970 | 1555 | FR | 2000 | Bilateral - Retrait Creys Génissiat 1 + essai HVDC FR IT | AT | 240 | Reduction because NTC over thermal limit on border
20231205 | 1130 | December | 7777 | 6807 | 2000 | 217 | 1320 | 214 | 2661 | Minimum Margin | Minimum Margin | 970 | 1555 | FR | 2000 | Bilateral - Retrait Creys Génissiat 1 + essai HVDC FR IT | AT | 240 | Reduction because NTC over thermal limit on border
20231205 | 1230 | December | 7300 | 6525 | 2000 | 203 | -2232 | -2232 | -1516 | TTC Selection - LTTC | TTC Selection - LTTC | 775 | 0 | FR | 2000 | Bilateral - Retrait Creys Génissiat 1 + essai HVDC FR IT | AT | 240 | Reduction because NTC over thermal limit on border
20231205 | 1330 | December | 7300 | 6525 | 2000 | 203 | -2232 | -2232 | -1516 | TTC Selection - LTTC | TTC Selection - LTTC | 775 | 0 | FR | 2000 | Bilateral - Retrait Creys Génissiat 1 + essai HVDC FR IT | AT | 240 | Reduction because NTC over thermal limit on border
20231205 | 1430 | December | 7300 | 6525 | 2000 | 203 | -2232 | -2232 | -1516 | TTC Selection - LTTC | TTC Selection - LTTC | 775 | 0 | FR | 2000 | Bilateral - Retrait Creys Génissiat 1 + essai HVDC FR IT | AT | 240 | Reduction because NTC over thermal limit on border
20231205 | 1530 | December | 7757 | 6796 | 2000 | 216 | 450 | 150 | 1760 | Minimum Margin | Minimum Margin | 961 | 1460 | FR | 2000 | Bilateral - Retrait Creys Génissiat 1 + essai HVDC FR IT | AT | 240 | Reduction because NTC over thermal limit on border
20231205 | 1630 | December | 7757 | 7296 | 2500 | 216 | 450 | 150 | 975 | Minimum Margin | Minimum Margin | 461 | 675 | FR | 2500 | Bilateral - Retrait Creys Génissiat 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231205 | 1730 | December | 8407 | 7563 | 2500 | 197 | -225 | -225 | 711 | Critical Branch | Validation phase | 844 | 711 | FR | 2500 | Bilateral - Retrait Creys Génissiat 1 | AT | 240 | Reduction because NTC over thermal limit on border | IT | 7567 | Correct value IT issue
20231205 | 1830 | December | 9000 | 8024 | 2500 | 217 | 2404 | 249 | 3437 | Minimum Margin | Validation phase | 976 | 1282 | FR | 2500 | Bilateral - Retrait Creys Génissiat 1 | AT | 240 | Reduction because NTC over thermal limit on border | IT | 8300 | N-2GOR-ROB SFI-ROB su PLL-SER 105%
20231205 | 1930 | December | 9000 | 8024 | 2500 | 217 | 2404 | 249 | 3437 | Minimum Margin | Validation phase | 976 | 1282 | FR | 2500 | Bilateral - Retrait Creys Génissiat 1 | AT | 240 | Reduction because NTC over thermal limit on border | IT | 8300 | N-2GOR-ROB SFI-ROB su PLL-SER 105%
20231205 | 2030 | December | 9000 | 8024 | 2500 | 217 | 2404 | 249 | 3437 | Minimum Margin | Validation phase | 976 | 1282 | FR | 2500 | Bilateral - Retrait Creys Génissiat 1 | AT | 240 | Reduction because NTC over thermal limit on border | IT | 8300 | N-2GOR-ROB SFI-ROB su PLL-SER 105%
20231205 | 2130 | December | 8415 | 7977 | 2500 | 215 | -1093 | -1093 | -689 | Critical Branch | Critical Branch | 438 | 0 | FR | 2500 | Bilateral - Retrait Creys Génissiat 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231205 | 2230 | December | 8415 | 7977 | 2500 | 215 | -1093 | -1093 | -689 | Critical Branch | Critical Branch | 438 | 0 | FR | 2500 | Bilateral - Retrait Creys Génissiat 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231205 | 2330 | December | 7605 | 7332 | 2500 | 199 | -271 | -271 | -21 | Critical Branch | Critical Branch | 273 | 0 | FR | 2500 | Bilateral - Retrait Creys Génissiat 1 | AT | 225 | Reduction because NTC over thermal limit on border
20231206 | 0030 | December | 8969 | 7750 | 2500 | 218 | -3549 | -3549 | -2191 | Critical Branch | Validation phase | 1219 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 225 | Reduction because NTC over thermal limit on border | IT | 8100 | N-2 ABV-GRA 1&2 su ABV-GRA3 105%
20231206 | 0130 | December | 8969 | 7750 | 2500 | 218 | -3549 | -3549 | -2191 | Critical Branch | Validation phase | 1219 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 225 | Reduction because NTC over thermal limit on border | IT | 8100 | N-2 ABV-GRA 1&amp;2 su ABV-GRA3 105%
20231206 | 0230 | December | 8969 | 7750 | 2500 | 218 | -3549 | -3549 | -2191 | Critical Branch | Validation phase | 1219 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 225 | Reduction because NTC over thermal limit on border | IT | 8100 | N-2 ABV-GRA 1&amp;2 su ABV-GRA3 105%
20231206 | 0330 | December | 7988 | 7565 | 2500 | 210 | -1320 | -1320 | -581 | Critical Branch | Critical Branch | 423 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 225 | Reduction because NTC over thermal limit on border
20231206 | 0430 | December | 7988 | 7565 | 2500 | 210 | -1320 | -1320 | -581 | Critical Branch | Critical Branch | 423 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 225 | Reduction because NTC over thermal limit on border
20231206 | 0530 | December | 7988 | 7565 | 2500 | 210 | -1320 | -1320 | -581 | Critical Branch | Critical Branch | 423 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 225 | Reduction because NTC over thermal limit on border
20231206 | 0630 | December | 7988 | 7565 | 2500 | 210 | -1320 | -1320 | -581 | Critical Branch | Critical Branch | 423 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 225 | Reduction because NTC over thermal limit on border
20231206 | 0730 | December | 8212 | 7186 | 2500 | 240 | -3773 | -3773 | -2793 | Critical Branch | Validation phase | 1026 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border | IT | 7800 | ABV GRA1 e 2 su ABV GRA 3 103%
20231206 | 0830 | December | 8212 | 7186 | 2500 | 240 | -3773 | -3773 | -2793 | Critical Branch | Validation phase | 1026 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border | IT | 7800 | ABV GRA1 e 2 su ABV GRA 3 103%
20231206 | 0930 | December | 6700 | 6466 | 2500 | 200 | -476 | -476 | -90 | TTC Selection - LTTC | TTC Selection - LTTC | 234 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231206 | 1030 | December | 6700 | 6466 | 2500 | 200 | -476 | -476 | -90 | TTC Selection - LTTC | TTC Selection - LTTC | 234 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231206 | 1130 | December | 6700 | 6466 | 2500 | 200 | -476 | -476 | -90 | TTC Selection - LTTC | TTC Selection - LTTC | 234 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231206 | 1230 | December | 6700 | 6466 | 2500 | 200 | -3641 | -3641 | -3370 | TTC Selection - LTTC | TTC Selection - LTTC | 234 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231206 | 1330 | December | 6700 | 6466 | 2500 | 200 | -3641 | -3641 | -3370 | TTC Selection - LTTC | TTC Selection - LTTC | 234 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231206 | 1430 | December | 6700 | 6466 | 2500 | 200 | -3641 | -3641 | -3370 | TTC Selection - LTTC | TTC Selection - LTTC | 234 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231206 | 1530 | December | 7592 | 6965 | 2500 | 228 | -3361 | -3361 | -2772 | Critical Branch | Critical Branch | 627 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231206 | 1630 | December | 7592 | 6965 | 2500 | 228 | -3361 | -3361 | -2772 | Critical Branch | Critical Branch | 627 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231206 | 1730 | December | 7992 | 7124 | 2500 | 217 | -3806 | -3806 | -2968 | Critical Branch | Validation phase | 868 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border | IT | 7402 | Correct value IT issue
20231206 | 1830 | December | 8051 | 7391 | 2500 | 231 | -4018 | -4018 | -3388 | Critical Branch | Critical Branch | 660 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231206 | 1930 | December | 8051 | 7391 | 2500 | 231 | -4018 | -4018 | -3388 | Critical Branch | Critical Branch | 660 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231206 | 2030 | December | 8051 | 7391 | 2500 | 231 | -4018 | -4018 | -3388 | Critical Branch | Critical Branch | 660 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231206 | 2130 | December | 8068 | 7401 | 2500 | 231 | -2343 | -2343 | -1731 | Critical Branch | Critical Branch | 667 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231206 | 2230 | December | 8068 | 7401 | 2500 | 231 | -2343 | -2343 | -1731 | Critical Branch | Critical Branch | 667 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231206 | 2330 | December | 7458 | 6942 | 2500 | 216 | -1727 | -1727 | -1257 | Critical Branch | Critical Branch | 516 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1 | AT | 225 | Reduction because NTC over thermal limit on border
20231207 | 0030 | December | 7502 | 6967 | 2500 | 218 | -1920 | -1920 | -1432 | Critical Branch | Critical Branch | 535 | 0 | FR | 2500 | Bilateral - RDCR CREYS GENISSIAT 1 | AT | 218 | Reduction because NTC over thermal limit on border
20231207 | 0130 | December | 7502 | 6967 | 2500 | 218 | -1920 | -1920 | -1432 | Critical Branch | Critical Branch | 535 | 0 | FR | 2500 | Bilateral - RDCR CREYS GENISSIAT 1 | AT | 218 | Reduction because NTC over thermal limit on border
20231207 | 0230 | December | 7502 | 6967 | 2500 | 218 | -1920 | -1920 | -1432 | Critical Branch | Critical Branch | 535 | 0 | FR | 2500 | Bilateral - RDCR CREYS GENISSIAT 1 | AT | 225 | Reduction because NTC over thermal limit on border
20231207 | 0330 | December | 7675 | 7065 | 2500 | 223 | -1798 | -1798 | -1244 | Critical Branch | Critical Branch | 610 | 0 | FR | 2500 | Bilateral - RDCR CREYS GENISSIAT 1 | AT | 225 | Reduction because NTC over thermal limit on border
20231207 | 0430 | December | 7675 | 7065 | 2500 | 223 | -1798 | -1798 | -1244 | Critical Branch | Critical Branch | 610 | 0 | FR | 2500 | Bilateral - RDCR CREYS GENISSIAT 1 | AT | 225 | Reduction because NTC over thermal limit on border
20231207 | 0530 | December | 7675 | 7065 | 2500 | 223 | -1798 | -1798 | -1244 | Critical Branch | Critical Branch | 610 | 0 | FR | 2500 | Bilateral - RDCR CREYS GENISSIAT 1 | AT | 225 | Reduction because NTC over thermal limit on border
20231207 | 0630 | December | 7675 | 7065 | 2500 | 223 | -1798 | -1798 | -1244 | Critical Branch | Critical Branch | 610 | 0 | FR | 2500 | Bilateral - RDCR CREYS GENISSIAT 1 | AT | 225 | Reduction because NTC over thermal limit on border
20231207 | 0730 | December | 7263 | 6933 | 2500 | 207 | -3244 | -3244 | -2938 | Critical Branch | Critical Branch | 330 | 0 | FR | 2500 | Bilateral - RDCR CREYS GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231207 | 0830 | December | 7263 | 6933 | 2500 | 207 | -3244 | -3244 | -2938 | Critical Branch | Critical Branch | 330 | 0 | FR | 2500 | Bilateral - RDCR CREYS GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231207 | 0930 | December | 7100 | 6838 | 2500 | 202 | -4148 | -4148 | -3896 | TTC Selection - LTTC | TTC Selection - LTTC | 262 | 0 | FR | 2500 | Bilateral - RDCR CREYS GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231207 | 1030 | December | 7100 | 6838 | 2500 | 202 | -4148 | -4148 | -3896 | TTC Selection - LTTC | TTC Selection - LTTC | 262 | 0 | FR | 2500 | Bilateral - RDCR CREYS GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231207 | 1130 | December | 7100 | 6838 | 2500 | 202 | -4148 | -4148 | -3896 | TTC Selection - LTTC | TTC Selection - LTTC | 262 | 0 | FR | 2500 | Bilateral - RDCR CREYS GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231207 | 1230 | December | 7100 | 6838 | 2500 | 202 | -4136 | -4136 | -3842 | TTC Selection - LTTC | TTC Selection - LTTC | 262 | 0 | FR | 2500 | Bilateral - RDCR CREYS GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231207 | 1330 | December | 7100 | 6838 | 2500 | 202 | -4136 | -4136 | -3842 | TTC Selection - LTTC | TTC Selection - LTTC | 262 | 0 | FR | 2500 | Bilateral - RDCR CREYS GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231207 | 1430 | December | 7100 | 6838 | 2500 | 202 | -4136 | -4136 | -3842 | TTC Selection - LTTC | TTC Selection - LTTC | 262 | 0 | FR | 2500 | Bilateral - RDCR CREYS GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231207 | 1530 | December | 7249 | 6925 | 2500 | 206 | -3349 | -3349 | -3049 | Critical Branch | Critical Branch | 324 | 0 | FR | 2500 | Bilateral - RDCR CREYS GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231207 | 1630 | December | 7249 | 6925 | 2500 | 206 | -3349 | -3349 | -3049 | Critical Branch | Critical Branch | 324 | 0 | FR | 2500 | Bilateral - RDCR CREYS GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231207 | 1730 | December | 7249 | 6925 | 2500 | 206 | -3349 | -3349 | -3049 | Critical Branch | Critical Branch | 324 | 0 | FR | 2500 | Bilateral - RDCR CREYS GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231207 | 1830 | December | 7100 | 7020 | 2682 | 202 | -2653 | -2653 | -2575 | TTC Selection - LTTC | TTC Selection - LTTC | 80 | 0 | FR | 2682 | Bilateral - RACR CREYS GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231207 | 1930 | December | 7100 | 7020 | 2682 | 202 | -2653 | -2653 | -2575 | TTC Selection - LTTC | TTC Selection - LTTC | 80 | 0 | FR | 2682 | Bilateral - RACR CREYS GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231207 | 2030 | December | 7100 | 7020 | 2682 | 202 | -2653 | -2653 | -2575 | TTC Selection - LTTC | TTC Selection - LTTC | 80 | 0 | FR | 2682 | Bilateral - RACR CREYS GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231207 | 2130 | December | 7736 | 7656 | 2948 | 221 | -3041 | -3041 | -2965 | Critical Branch | Critical Branch | 80 | 0 | FR | 2948 | Bilateral - RACR CREYS GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231207 | 2230 | December | 7736 | 7656 | 2948 | 221 | -3041 | -3041 | -2965 | Critical Branch | Critical Branch | 80 | 0 | FR | 2948 | Bilateral - RACR CREYS GENISSIAT 1 | AT | 240 | Reduction because NTC over thermal limit on border
20231207 | 2330 | December | 7126 | 6947 | 2693 | 206 | -2432 | -2432 | -2263 | Critical Branch | Critical Branch | 179 | 0 | FR | 2693 | Bilateral - RACR CREYS GENISSIAT 1 | AT | 225 | Reduction because NTC over thermal limit on border
20231208 | 0030 | December | 6590 | 6568 | 2640 | 167 | -5585 | -5585 | -5562 | TTC Selection - LTTC | TTC Selection - LTTC | 22 | 0 | AT | 167 | Bilateral - Reduction because NTC over thermal limit on border
20231208 | 0130 | December | 6590 | 6568 | 2640 | 167 | -5585 | -5585 | -5562 | TTC Selection - LTTC | TTC Selection - LTTC | 22 | 0 | AT | 167 | Bilateral - Reduction because NTC over thermal limit on border
20231208 | 0730 | December | 7903 | 7740 | 3138 | 225 | -1284 | -1284 | -1121 | Critical Branch | Validation phase | 163 | 0 | CH | 7550 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20231208 | 0830 | December | 6603 | 6440 | 1838 | 225 | -113 | -113 | 50 | Critical Branch | Validation phase | 163 | 50 | CH | 6250 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20231208 | 0930 | December | 6646 | 6440 | 1838 | 225 | -2758 | -2758 | -2552 | Critical Branch | Validation phase | 206 | 0 | CH | 6250 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20231208 | 1030 | December | 6646 | 6440 | 1838 | 225 | -2758 | -2758 | -2552 | Critical Branch | Validation phase | 206 | 0 | CH | 6250 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20231208 | 1130 | December | 6646 | 6440 | 1838 | 225 | -2758 | -2758 | -2552 | Critical Branch | Validation phase | 206 | 0 | CH | 6250 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20231208 | 1230 | December | 6837 | 6440 | 1838 | 225 | -1052 | -1052 | -655 | Critical Branch | Validation phase | 397 | 0 | CH | 6250 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20231208 | 1330 | December | 6837 | 6440 | 1838 | 225 | -1052 | -1052 | -655 | Critical Branch | Validation phase | 397 | 0 | CH | 6250 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20231208 | 1430 | December | 6837 | 6440 | 1838 | 225 | -1052 | -1052 | -655 | Critical Branch | Validation phase | 397 | 0 | CH | 6250 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20231208 | 1830 | December | 7836 | 7740 | 3138 | 225 | -2905 | -2905 | -2809 | Critical Branch | Validation phase | 96 | 0 | CH | 7550 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20231208 | 1930 | December | 7836 | 7740 | 3138 | 225 | -2905 | -2905 | -2809 | Critical Branch | Validation phase | 96 | 0 | CH | 7550 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20231208 | 2030 | December | 7836 | 7740 | 3138 | 225 | -2905 | -2905 | -2809 | Critical Branch | Validation phase | 96 | 0 | CH | 7550 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20231208 | 2130 | December | 7988 | 7740 | 3138 | 225 | -2650 | -2650 | -2402 | Critical Branch | Validation phase | 248 | 0 | CH | 7550 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20231208 | 2230 | December | 7988 | 7740 | 3138 | 225 | -2650 | -2650 | -2402 | Critical Branch | Validation phase | 248 | 0 | CH | 7550 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20231208 | 2330 | December | 7988 | 7740 | 3138 | 225 | -2650 | -2650 | -2402 | Critical Branch | Validation phase | 248 | 0 | CH | 7550 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20231209 | 0830 | December | 5800 | 5742 | 1548 | 194 | -7062 | -7062 | -7000 | TTC Selection - LTTC | TTC Selection - LTTC | 58 | 0 | FR | 1548 | Bilateral - RDCR VENAUS - VILLARODIN | AT | 240 | Reduction because od outage of line 912
20231210 | 1230 | December | 8377 | 8276 | 3138 | 225 | -5760 | -5760 | -5659 | Critical Branch | Validation phase | 101 | 0 | CH | 8086 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20231210 | 1330 | December | 8377 | 8276 | 3138 | 225 | -5760 | -5760 | -5659 | Critical Branch | Validation phase | 101 | 0 | CH | 8086 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20231210 | 1430 | December | 8377 | 8276 | 3138 | 225 | -5760 | -5760 | -5659 | Critical Branch | Validation phase | 101 | 0 | CH | 8086 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20231210 | 1530 | December | 9145 | 8276 | 3138 | 225 | -3075 | -3075 | -2206 | Critical Branch | Validation phase | 869 | 0 | CH | 8086 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20231210 | 1630 | December | 9145 | 8276 | 3138 | 225 | -3075 | -3075 | -2206 | Critical Branch | Validation phase | 869 | 0 | CH | 8086 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20231210 | 1730 | December | 9145 | 8276 | 3138 | 225 | -3075 | -3075 | -2206 | Critical Branch | Validation phase | 869 | 0 | CH | 8086 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20231210 | 1830 | December | 9290 | 8490 | 2924 | 210 | -3247 | -3247 | -2447 | Critical Branch | Validation phase | 800 | 0 | IT | 8300 | N-1 ABV-RON2 -> ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231210 | 1930 | December | 9290 | 8490 | 2924 | 210 | -3247 | -3247 | -2447 | Critical Branch | Validation phase | 800 | 0 | IT | 8300 | N-1 ABV-RON2 -> ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231210 | 2030 | December | 9290 | 8490 | 2924 | 210 | -3247 | -3247 | -2447 | Critical Branch | Validation phase | 800 | 0 | IT | 8300 | N-1 ABV-RON2 -> ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231210 | 2130 | December | 8922 | 8322 | 2862 | 205 | -1691 | -1691 | -1091 | Critical Branch | Validation phase | 600 | 0 | IT | 8132 | N-1 ABV-RON2 -> ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231210 | 2230 | December | 8922 | 8322 | 2862 | 205 | -1691 | -1691 | -1091 | Critical Branch | Validation phase | 600 | 0 | IT | 8132 | N-1 ABV-RON2 -> ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231211 | 0030 | December | 9155 | 7990 | 2923 | 210 | -3842 | -3842 | -2677 | Critical Branch | Validation phase | 1165 | 0 | IT | 7800 | ABV-GRA 1-2 on ABV-GRA 3, RON-ABV1 on RON-ABV2 and ABV-RON1-2 on VNS-VLR
20231211 | 0130 | December | 9155 | 7990 | 2923 | 210 | -3842 | -3842 | -2677 | Critical Branch | Validation phase | 1165 | 0 | IT | 7800 | ABV-GRA 1-2 on ABV-GRA 3, RON-ABV1 on RON-ABV2 and ABV-RON1-2 on VNS-VLR
20231211 | 0230 | December | 9155 | 7990 | 2923 | 210 | -3842 | -3842 | -2677 | Critical Branch | Validation phase | 1165 | 0 | IT | 7800 | ABV-GRA 1-2 on ABV-GRA 3, RON-ABV1 on RON-ABV2 and ABV-RON1-2 on VNS-VLR
20231211 | 0330 | December | 8920 | 7990 | 2923 | 210 | -3630 | -3630 | -2700 | Critical Branch | Validation phase | 930 | 0 | IT | 7800 | ABV-GRA 1-2 on ABV-GRA 3, RON-ABV1 on RON-ABV2 and ABV-RON1-2 on VNS-VLR
20231211 | 0430 | December | 8920 | 7990 | 2923 | 210 | -3630 | -3630 | -2700 | Critical Branch | Validation phase | 930 | 0 | IT | 7800 | ABV-GRA 1-2 on ABV-GRA 3, RON-ABV1 on RON-ABV2 and ABV-RON1-2 on VNS-VLR
20231211 | 0530 | December | 8920 | 7990 | 2923 | 210 | -3630 | -3630 | -2700 | Critical Branch | Validation phase | 930 | 0 | IT | 7800 | ABV-GRA 1-2 on ABV-GRA 3, RON-ABV1 on RON-ABV2 and ABV-RON1-2 on VNS-VLR
20231211 | 0630 | December | 8920 | 7990 | 2923 | 210 | -3630 | -3630 | -2700 | Critical Branch | Validation phase | 930 | 0 | IT | 7800 | ABV-GRA 1-2 on ABV-GRA 3, RON-ABV1 on RON-ABV2 and ABV-RON1-2 on VNS-VLR
20231211 | 0730 | December | 9242 | 7990 | 2959 | 216 | -2114 | -2114 | -862 | Critical Branch | Validation phase | 1252 | 0 | IT | 7800 | ABV-GRA 1-2 on ABV-GRA 3, RON-ABV1 on RON-ABV2 and ABV-RON1-2 on VNS-VLR
20231211 | 0830 | December | 9242 | 7990 | 2959 | 216 | -2114 | -2114 | -862 | Critical Branch | Validation phase | 1252 | 0 | IT | 7800 | ABV-GRA 1-2 on ABV-GRA 3, RON-ABV1 on RON-ABV2 and ABV-RON1-2 on VNS-VLR
20231211 | 1230 | December | 7564 | 7503 | 2730 | 204 | -2447 | -2447 | -2373 | TTC Selection - LTTC | TTC Selection - LTTC | 61 | 0 | FR | 2730 | Bilateral - Essais FIL | AT | 240 | Reduction because of disconnection of line 261 and outage of line 912
20231212 | 0030 | December | 8431 | 7540 | 2827 | 0 | -3884 | -3884 | -2993 | Critical Branch | Validation phase | 891 | 0 | IT | 7350 | ABV-GRA 1-2 on ABV-GRA 3, RON-ABV1 on RON-ABV2 and ABV-RON1-2 on VNS-VLR
20231212 | 0130 | December | 8431 | 7540 | 2827 | 0 | -3884 | -3884 | -2993 | Critical Branch | Validation phase | 891 | 0 | IT | 7350 | ABV-GRA 1-2 on ABV-GRA 3, RON-ABV1 on RON-ABV2 and ABV-RON1-2 on VNS-VLR
20231212 | 0230 | December | 8431 | 7540 | 2827 | 0 | -3884 | -3884 | -2993 | Critical Branch | Validation phase | 891 | 0 | IT | 7350 | ABV-GRA 1-2 on ABV-GRA 3, RON-ABV1 on RON-ABV2 and ABV-RON1-2 on VNS-VLR
20231212 | 0330 | December | 8254 | 7540 | 2827 | 0 | -3247 | -3247 | -2533 | Critical Branch | Validation phase | 714 | 0 | IT | 7350 | ABV-GRA 1-2 on ABV-GRA 3, RON-ABV1 on RON-ABV2 and ABV-RON1-2 on VNS-VLR
20231212 | 0430 | December | 8254 | 7540 | 2827 | 0 | -3247 | -3247 | -2533 | Critical Branch | Validation phase | 714 | 0 | IT | 7350 | ABV-GRA 1-2 on ABV-GRA 3, RON-ABV1 on RON-ABV2 and ABV-RON1-2 on VNS-VLR
20231212 | 0530 | December | 8254 | 7540 | 2827 | 0 | -3247 | -3247 | -2533 | Critical Branch | Validation phase | 714 | 0 | IT | 7350 | ABV-GRA 1-2 on ABV-GRA 3, RON-ABV1 on RON-ABV2 and ABV-RON1-2 on VNS-VLR
20231212 | 0630 | December | 8254 | 7540 | 2827 | 0 | -3247 | -3247 | -2533 | Critical Branch | Validation phase | 714 | 0 | IT | 7350 | ABV-GRA 1-2 on ABV-GRA 3, RON-ABV1 on RON-ABV2 and ABV-RON1-2 on VNS-VLR
20231212 | 1830 | December | 8798 | 8040 | 2877 | 0 | -2461 | -2461 | -1703 | Critical Branch | Validation phase | 758 | 0 | IT | 7850 | ABV-GRA 1-2 on ABV-GRA 3, RON-ABV1 on RON-ABV2 and ABV-RON1-2 on VNS-VLR
20231212 | 1930 | December | 8798 | 8040 | 2877 | 0 | -2461 | -2461 | -1703 | Critical Branch | Validation phase | 758 | 0 | IT | 7850 | ABV-GRA 1-2 on ABV-GRA 3, RON-ABV1 on RON-ABV2 and ABV-RON1-2 on VNS-VLR
20231212 | 2030 | December | 8798 | 8040 | 2877 | 0 | -2461 | -2461 | -1703 | Critical Branch | Validation phase | 758 | 0 | IT | 7850 | ABV-GRA 1-2 on ABV-GRA 3, RON-ABV1 on RON-ABV2 and ABV-RON1-2 on VNS-VLR
20231212 | 2130 | December | 8943 | 8040 | 2877 | 0 | -4830 | -4830 | -3927 | Critical Branch | Validation phase | 903 | 0 | IT | 7850 | ABV-GRA 1-2 on ABV-GRA 3, RON-ABV1 on RON-ABV2 and ABV-RON1-2 on VNS-VLR
20231212 | 2230 | December | 8943 | 8040 | 2877 | 0 | -4830 | -4830 | -3927 | Critical Branch | Validation phase | 903 | 0 | IT | 7850 | ABV-GRA 1-2 on ABV-GRA 3, RON-ABV1 on RON-ABV2 and ABV-RON1-2 on VNS-VLR
20231213 | 1230 | December | 8706 | 7490 | 2667 | 0 | -4671 | -4671 | -3455 | Critical Branch | Validation phase | 1216 | 0 | IT | 7300 | ABV-GRA 1-2 on ABV-GRA 3, RON-ABV1 on RON-ABV2 and ABV-RON1-2 on VNS-VLR
20231213 | 1330 | December | 8706 | 7490 | 2667 | 0 | -4671 | -4671 | -3455 | Critical Branch | Validation phase | 1216 | 0 | IT | 7300 | ABV-GRA 1-2 on ABV-GRA 3, RON-ABV1 on RON-ABV2 and ABV-RON1-2 on VNS-VLR
20231213 | 1430 | December | 8706 | 7490 | 2667 | 0 | -4671 | -4671 | -3455 | Critical Branch | Validation phase | 1216 | 0 | IT | 7300 | ABV-GRA 1-2 on ABV-GRA 3, RON-ABV1 on RON-ABV2 and ABV-RON1-2 on VNS-VLR
20231213 | 1530 | December | 7860 | 7490 | 2667 | 0 | -3842 | -3842 | -3472 | TTC Selection - LTTC | Validation phase | 370 | 0 | IT | 7300 | ABV-GRA 1-2 on ABV-GRA 3, RON-ABV1 on RON-ABV2 and ABV-RON1-2 on VNS-VLR
20231213 | 1630 | December | 7860 | 7490 | 2667 | 0 | -3842 | -3842 | -3472 | TTC Selection - LTTC | Validation phase | 370 | 0 | IT | 7300 | ABV-GRA 1-2 on ABV-GRA 3, RON-ABV1 on RON-ABV2 and ABV-RON1-2 on VNS-VLR
20231213 | 1730 | December | 7860 | 7490 | 2667 | 0 | -3842 | -3842 | -3472 | TTC Selection - LTTC | Validation phase | 370 | 0 | IT | 7300 | ABV-GRA 1-2 on ABV-GRA 3, RON-ABV1 on RON-ABV2 and ABV-RON1-2 on VNS-VLR
20231213 | 1830 | December | 7860 | 7490 | 2667 | 0 | -4351 | -4351 | -3981 | TTC Selection - LTTC | Validation phase | 370 | 0 | IT | 7300 | ABV-GRA 1-2 on ABV-GRA 3, RON-ABV1 on RON-ABV2 and ABV-RON1-2 on VNS-VLR
20231213 | 1930 | December | 7860 | 7490 | 2667 | 0 | -4351 | -4351 | -3981 | TTC Selection - LTTC | Validation phase | 370 | 0 | IT | 7300 | ABV-GRA 1-2 on ABV-GRA 3, RON-ABV1 on RON-ABV2 and ABV-RON1-2 on VNS-VLR
20231213 | 2030 | December | 7860 | 7490 | 2667 | 0 | -4351 | -4351 | -3981 | TTC Selection - LTTC | Validation phase | 370 | 0 | IT | 7300 | ABV-GRA 1-2 on ABV-GRA 3, RON-ABV1 on RON-ABV2 and ABV-RON1-2 on VNS-VLR
20231213 | 2130 | December | 7860 | 7490 | 2667 | 0 | -4881 | -4881 | -4511 | TTC Selection - LTTC | Validation phase | 370 | 0 | IT | 7300 | ABV-GRA 1-2 on ABV-GRA 3, RON-ABV1 on RON-ABV2 and ABV-RON1-2 on VNS-VLR
20231213 | 2230 | December | 7860 | 7490 | 2667 | 0 | -4881 | -4881 | -4511 | TTC Selection - LTTC | Validation phase | 370 | 0 | IT | 7300 | ABV-GRA 1-2 on ABV-GRA 3, RON-ABV1 on RON-ABV2 and ABV-RON1-2 on VNS-VLR
20231214 | 0030 | December | 7465 | 5017 | 1814 | 0 | -4832 | -4832 | -2412 | TTC Selection - LTTC | Validation phase | 2448 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | IT | 5000 | Allocation Constraints
20231214 | 0130 | December | 7465 | 5017 | 1814 | 0 | -4832 | -4832 | -2412 | TTC Selection - LTTC | Validation phase | 2448 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | IT | 5000 | Allocation Constraints
20231214 | 0230 | December | 7465 | 5017 | 1814 | 0 | -4832 | -4832 | -2412 | TTC Selection - LTTC | Validation phase | 2448 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | IT | 5000 | Allocation Constraints
20231214 | 0330 | December | 7465 | 5017 | 1814 | 0 | -4142 | -4142 | -1728 | TTC Selection - LTTC | Validation phase | 2448 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | IT | 5000 | Allocation Constraints
20231214 | 0430 | December | 7465 | 5017 | 1814 | 0 | -4142 | -4142 | -1728 | TTC Selection - LTTC | Validation phase | 2448 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | IT | 5000 | Allocation Constraints
20231214 | 0530 | December | 7465 | 5017 | 1814 | 0 | -4142 | -4142 | -1728 | TTC Selection - LTTC | Validation phase | 2448 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | IT | 5000 | Allocation Constraints
20231214 | 0630 | December | 7465 | 5017 | 1814 | 0 | -4142 | -4142 | -1728 | TTC Selection - LTTC | Validation phase | 2448 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | IT | 5000 | Allocation Constraints
20231214 | 0730 | December | 8160 | 5032 | 1729 | 0 | -5272 | -5272 | -2172 | TTC Selection - LTTC | Validation phase | 3128 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | IT | 5000 | Allocation Constraints
20231214 | 0830 | December | 8160 | 5032 | 1729 | 0 | -5272 | -5272 | -2172 | TTC Selection - LTTC | Validation phase | 3128 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | IT | 5000 | Allocation Constraints
20231214 | 0930 | December | 9410 | 5032 | 1729 | 0 |  |  |  | Scheduled TTC | Validation phase | 4378 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | IT | 5000 | Allocation Constraints
20231214 | 1030 | December | 9410 | 5032 | 1729 | 0 |  |  |  | Scheduled TTC | Validation phase | 4378 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | IT | 5000 | Allocation Constraints
20231214 | 1130 | December | 9410 | 5032 | 1729 | 0 |  |  |  | Scheduled TTC | Validation phase | 4378 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | IT | 5000 | Allocation Constraints
20231214 | 1230 | December | 8160 | 5032 | 1729 | 0 | -6359 | -6359 | -3246 | TTC Selection - LTTC | Validation phase | 3128 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | IT | 5000 | Allocation Constraints
20231214 | 1330 | December | 8160 | 6532 | 2301 | 0 | -6359 | -6359 | -4746 | TTC Selection - LTTC | Smoothing ramp | 1628 | 0 | Smoothing
20231214 | 1430 | December | 8160 | 7902 | 2824 | 0 | -6359 | -6359 | -6116 | TTC Selection - LTTC | TTC Selection - LTTC | 258 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231214 | 1530 | December | 8160 | 7902 | 2824 | 0 | -6255 | -6255 | -6013 | TTC Selection - LTTC | TTC Selection - LTTC | 258 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231214 | 1630 | December | 8160 | 7902 | 2824 | 0 | -6255 | -6255 | -6013 | TTC Selection - LTTC | TTC Selection - LTTC | 258 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231214 | 1730 | December | 8160 | 7902 | 2824 | 0 | -6255 | -6255 | -6013 | TTC Selection - LTTC | TTC Selection - LTTC | 258 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231214 | 1830 | December | 8160 | 7902 | 2824 | 0 | -4365 | -4365 | -4146 | TTC Selection - LTTC | TTC Selection - LTTC | 258 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231214 | 1930 | December | 8160 | 7902 | 2824 | 0 | -4365 | -4365 | -4146 | TTC Selection - LTTC | TTC Selection - LTTC | 258 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231214 | 2030 | December | 8160 | 7902 | 2824 | 0 | -4365 | -4365 | -4146 | TTC Selection - LTTC | TTC Selection - LTTC | 258 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231214 | 2130 | December | 8160 | 7902 | 2824 | 0 | -5780 | -5780 | -5545 | TTC Selection - LTTC | TTC Selection - LTTC | 258 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231214 | 2230 | December | 8160 | 7902 | 2824 | 0 | -5780 | -5780 | -5545 | TTC Selection - LTTC | TTC Selection - LTTC | 258 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231214 | 2330 | December | 7365 | 7111 | 2655 | 0 | -5008 | -5008 | -4778 | TTC Selection - LTTC | TTC Selection - LTTC | 254 | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231215 | 0730 | December | 9360 | 9277 | 3894 | 260 | -5361 | -5361 | -5278 | TTC Selection - LTTC | Validation phase | 83 | 0 | CH | 9087 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231215 | 0830 | December | 9360 | 9277 | 3894 | 260 | -5361 | -5361 | -5278 | TTC Selection - LTTC | Validation phase | 83 | 0 | CH | 9087 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231215 | 1130 | December | 9360 | 9287 | 3898 | 261 | -5357 | -5357 | -5284 | TTC Selection - LTTC | Smoothing ramp | 73 | 0 | Smoothing
20231215 | 1230 | December | 9584 | 7787 | 3233 | 216 | -4975 | -4975 | -3178 | Critical Branch | Validation phase | 1797 | 0 | CH | 7597 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231215 | 1330 | December | 9584 | 7787 | 3233 | 216 | -4975 | -4975 | -3178 | Critical Branch | Validation phase | 1797 | 0 | CH | 7597 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231215 | 1430 | December | 9584 | 7787 | 3233 | 216 | -4975 | -4975 | -3178 | Critical Branch | Validation phase | 1797 | 0 | CH | 7597 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231215 | 1530 | December | 9360 | 9235 | 3875 | 259 | -5522 | -5522 | -5397 | TTC Selection - LTTC | Validation phase | 125 | 0 | CH | 9045 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231215 | 1630 | December | 9360 | 9235 | 3875 | 259 | -5522 | -5522 | -5397 | TTC Selection - LTTC | Validation phase | 125 | 0 | CH | 9045 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231215 | 1730 | December | 9360 | 9235 | 3875 | 259 | -5522 | -5522 | -5397 | TTC Selection - LTTC | Validation phase | 125 | 0 | CH | 9045 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231215 | 1830 | December | 10119 | 9816 | 4133 | 276 | -5903 | -5903 | -5600 | Critical Branch | Validation phase | 303 | 0 | CH | 9626 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231215 | 1930 | December | 10359 | 10056 | 4141 | 499 | -6115 | -6115 | -5812 | Critical Branch | Validation phase | 303 | 0 | CH | 9866 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231215 | 2030 | December | 10359 | 10056 | 4141 | 499 | -6115 | -6115 | -5812 | Critical Branch | Validation phase | 303 | 0 | CH | 9866 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231215 | 2130 | December | 10062 | 9602 | 3944 | 475 | -4646 | -4646 | -4186 | Critical Branch | Validation phase | 460 | 0 | CH | 9412 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231215 | 2230 | December | 10062 | 9602 | 3944 | 475 | -4646 | -4646 | -4186 | Critical Branch | Validation phase | 460 | 0 | CH | 9412 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231215 | 2330 | December | 9252 | 8792 | 3771 | 456 | -3787 | -3787 | -3327 | Critical Branch | Validation phase | 460 | 0 | CH | 8602 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231216 | 0030 | December | 9765 | 8156 | No result | No result | -5914 | -5914 | -4305 | Critical Branch | Validation phase | 1609 | 0 | CH | 7966 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231216 | 0130 | December | 9765 | 8156 | No result | No result | -5914 | -5914 | -4305 | Critical Branch | Validation phase | 1609 | 0 | CH | 7966 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231216 | 0230 | December | 9765 | 8156 | No result | No result | -5914 | -5914 | -4305 | Critical Branch | Validation phase | 1609 | 0 | CH | 7966 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231216 | 0730 | December | 9600 | 9500 | No result | No result | -7851 | -7851 | -7751 | TTC Selection - LTTC | Validation phase | 100 | 0 | IT | 9310 | N-2 ABV-RON1&2 on VNS-VLR(101%)
20231216 | 0830 | December | 9600 | 9500 | No result | No result | -7851 | -7851 | -7751 | TTC Selection - LTTC | Validation phase | 100 | 0 | IT | 9310 | N-2 ABV-RON1&amp;2 on VNS-VLR(101%)
20231216 | 0930 | December | 9600 | 9500 | No result | No result | -7613 | -7613 | -7513 | TTC Selection - LTTC | Validation phase | 100 | 0 | IT | 9310 | N-2 ABV-RON1&amp;2 on VNS-VLR(101%)
20231216 | 1030 | December | 9600 | 9500 | No result | No result | -7613 | -7613 | -7513 | TTC Selection - LTTC | Validation phase | 100 | 0 | IT | 9310 | N-2 ABV-RON1&amp;2 on VNS-VLR(101%)
20231216 | 1130 | December | 9600 | 9500 | No result | No result | -7613 | -7613 | -7513 | TTC Selection - LTTC | Validation phase | 100 | 0 | IT | 9310 | N-2 ABV-RON1&amp;2 on VNS-VLR(101%)
20231216 | 1230 | December | 9600 | 9500 | No result | No result | -7895 | -7895 | -7795 | TTC Selection - LTTC | Validation phase | 100 | 0 | IT | 9310 | N-2 ABV-RON1&amp;2 on VNS-VLR(101%)
20231216 | 1330 | December | 9600 | 9500 | No result | No result | -7895 | -7895 | -7795 | TTC Selection - LTTC | Validation phase | 100 | 0 | IT | 9310 | N-2 ABV-RON1&amp;2 on VNS-VLR(101%)
20231216 | 1430 | December | 9600 | 9500 | No result | No result | -7895 | -7895 | -7795 | TTC Selection - LTTC | Validation phase | 100 | 0 | IT | 9310 | N-2 ABV-RON1&amp;2 on VNS-VLR(101%)
20231216 | 1530 | December | 9600 | 9500 | No result | No result | -5948 | -5948 | -5848 | TTC Selection - LTTC | Validation phase | 100 | 0 | IT | 9310 | N-2 ABV-RON1&amp;2 on VNS-VLR(101%)
20231216 | 1630 | December | 9600 | 9500 | No result | No result | -5948 | -5948 | -5848 | TTC Selection - LTTC | Validation phase | 100 | 0 | IT | 9310 | N-2 ABV-RON1&amp;2 on VNS-VLR(101%)
20231216 | 1730 | December | 9600 | 9500 | No result | No result | -5948 | -5948 | -5848 | TTC Selection - LTTC | Validation phase | 100 | 0 | IT | 9310 | N-2 ABV-RON1&amp;2 on VNS-VLR(101%)
20231216 | 1830 | December | 9600 | 9500 | No result | No result | -3664 | -3664 | -3564 | TTC Selection - LTTC | Validation phase | 100 | 0 | IT | 9310 | N-2 ABV-RON1&amp;2 on VNS-VLR(101%)
20231216 | 1930 | December | 9600 | 9500 | No result | No result | -3664 | -3664 | -3564 | TTC Selection - LTTC | Validation phase | 100 | 0 | IT | 9310 | N-2 ABV-RON1&amp;2 on VNS-VLR(101%)
20231216 | 2030 | December | 9600 | 9500 | No result | No result | -3664 | -3664 | -3564 | TTC Selection - LTTC | Validation phase | 100 | 0 | IT | 9310 | N-2 ABV-RON1&amp;2 on VNS-VLR(101%)
20231216 | 2130 | December | 10870 | 8923 | No result | No result | -5799 | -5799 | -3852 | Critical Branch | Validation phase | 1947 | 0 | CH | 8733 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231216 | 2230 | December | 10870 | 8923 | No result | No result | -5799 | -5799 | -3852 | Critical Branch | Validation phase | 1947 | 0 | CH | 8733 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231216 | 2330 | December | 10060 | 8113 | No result | No result | -4986 | -4986 | -3039 | Critical Branch | Validation phase | 1947 | 0 | CH | 7923 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231217 | 0030 | December | 10432 | 10410 | 4516 | 525 | -7992 | -7992 | -7969 | Critical Branch | Critical Branch | 22 | 0 | AT | 525 | Bilateral - Reduction because NTC over thermal limit on border
20231217 | 0130 | December | 10432 | 10410 | 4516 | 525 | -7992 | -7992 | -7969 | Critical Branch | Critical Branch | 22 | 0 | AT | 525 | Bilateral - Reduction because NTC over thermal limit on border
20231217 | 0230 | December | 10432 | 10410 | 4516 | 525 | -7992 | -7992 | -7969 | Critical Branch | Critical Branch | 22 | 0 | AT | 525 | Bilateral - Reduction because NTC over thermal limit on border
20231217 | 0330 | December | 10636 | 10467 | 4543 | 525 | -4165 | -4165 | -3995 | Critical Branch | Validation phase | 169 | 0 | AT | 525 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | CH | 10302 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231217 | 0430 | December | 10636 | 10467 | 4543 | 525 | -4165 | -4165 | -3995 | Critical Branch | Validation phase | 169 | 0 | AT | 525 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | CH | 10302 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231217 | 0530 | December | 10636 | 10467 | 4543 | 525 | -4165 | -4165 | -3995 | Critical Branch | Validation phase | 169 | 0 | AT | 525 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | CH | 10302 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231217 | 0630 | December | 10636 | 10467 | 4543 | 525 | -4165 | -4165 | -3995 | Critical Branch | Validation phase | 169 | 0 | AT | 525 | Bilateral - Reduction because NTC over thermal limit on border |  |  |  | CH | 10302 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231218 | 0730 | December | 10560 | 10160 | 4415 | 532 | -1801 | -1801 | -1401 | Critical Branch | Validation phase | 400 | 0 | IT | 9970 | N-1 380 kV ROB-GOR&ROB-SFI -> 380kV SIL-SOA
20231218 | 0830 | December | 10560 | 10160 | 4415 | 532 | -1801 | -1801 | -1401 | Critical Branch | Validation phase | 400 | 0 | IT | 9970 | N-1 380 kV ROB-GOR&amp;ROB-SFI -&gt; 380kV SIL-SOA
20231218 | 0930 | December | 10283 | 10160 | 4415 | 532 | -6470 | -6470 | -6347 | Critical Branch | Validation phase | 123 | 0 | IT | 9970 | N-1 380 kV ROB-GOR&amp;ROB-SFI -&gt; 380kV SIL-SOA
20231218 | 1030 | December | 10283 | 10160 | 4415 | 532 | -6470 | -6470 | -6347 | Critical Branch | Validation phase | 123 | 0 | IT | 9970 | N-1 380 kV ROB-GOR&amp;ROB-SFI -&gt; 380kV SIL-SOA
20231218 | 1130 | December | 10283 | 10160 | 4415 | 532 | -6470 | -6470 | -6347 | Critical Branch | Validation phase | 123 | 0 | IT | 9970 | N-1 380 kV ROB-GOR&amp;ROB-SFI -&gt; 380kV SIL-SOA
20231218 | 1830 | December | 10452 | 10160 | 4415 | 532 | -3657 | -3657 | -3365 | Critical Branch | Validation phase | 292 | 0 | IT | 9970 | N-1 380 kV ROB-GOR&amp;amp;ROB-SFI -&amp;gt; 380kV SIL-SOA
20231218 | 1930 | December | 10452 | 10160 | 4415 | 532 | -3657 | -3657 | -3365 | Critical Branch | Validation phase | 292 | 0 | IT | 9970 | N-1 380 kV ROB-GOR&amp;amp;ROB-SFI -&amp;gt; 380kV SIL-SOA
20231218 | 2030 | December | 10452 | 10160 | 4415 | 532 | -3657 | -3657 | -3365 | Critical Branch | Validation phase | 292 | 0 | IT | 9970 | N-1 380 kV ROB-GOR&amp;amp;ROB-SFI -&amp;gt; 380kV SIL-SOA
20231219 | 1230 | December | 10141 | 9641 | 3961 | 477 | -4315 | -4315 | -3815 | Critical Branch | Validation phase | 500 | 0 | IT | 9451 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo-Musignano, C: N-1 Soazza-Bulciago
20231219 | 1330 | December | 10141 | 9641 | 3961 | 477 | -4315 | -4315 | -3815 | Critical Branch | Validation phase | 500 | 0 | IT | 9451 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo-Musignano, C: N-1 Soazza-Bulciago
20231219 | 1430 | December | 10141 | 9641 | 3961 | 477 | -4315 | -4315 | -3815 | Critical Branch | Validation phase | 500 | 0 | IT | 9451 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo-Musignano, C: N-1 Soazza-Bulciago
20231222 | 0030 | December | 8890 | 8275 | 3200 | 462 | -6435 | -6435 | -5827 | TTC Selection - LTTC | TTC Selection - LTTC | 615 | 0 | FR | 3200 | Bilateral - Avarie HVDC Gde Ile-Piossasco
20231222 | 0130 | December | 8890 | 8275 | 3200 | 462 | -6435 | -6435 | -5827 | TTC Selection - LTTC | TTC Selection - LTTC | 615 | 0 | FR | 3200 | Bilateral - Avarie HVDC Gde Ile-Piossasco
20231222 | 0230 | December | 8890 | 8275 | 3200 | 462 | -6435 | -6435 | -5827 | TTC Selection - LTTC | TTC Selection - LTTC | 615 | 0 | FR | 3200 | Bilateral - Avarie HVDC Gde Ile-Piossasco
20231222 | 0330 | December | 10040 | 8684 | 3200 | 503 |  |  |  | Scheduled TTC | Validation phase | 1356 | 0 | FR | 3200 | Bilateral - Avarie HVDC Gde Ile-Piossasco |  |  |  | IT | 9450 | N-1 ABV-RON2 -> ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231222 | 0430 | December | 10040 | 8684 | 3200 | 503 |  |  |  | Scheduled TTC | Validation phase | 1356 | 0 | FR | 3200 | Bilateral - Avarie HVDC Gde Ile-Piossasco |  |  |  | IT | 9450 | N-1 ABV-RON2 -> ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231222 | 0530 | December | 10040 | 8684 | 3200 | 503 |  |  |  | Scheduled TTC | Validation phase | 1356 | 0 | FR | 3200 | Bilateral - Avarie HVDC Gde Ile-Piossasco |  |  |  | IT | 9450 | N-1 ABV-RON2 -> ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231222 | 0630 | December | 10040 | 8684 | 3200 | 503 |  |  |  | Scheduled TTC | Validation phase | 1356 | 0 | FR | 3200 | Bilateral - Avarie HVDC Gde Ile-Piossasco |  |  |  | IT | 9450 | N-1 ABV-RON2 -> ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid,
20231222 | 0730 | December | 9600 | 8857 | 3200 | 475 | -7890 | -7890 | -7149 | TTC Selection - LTTC | TTC Selection - LTTC | 743 | 0 | FR | 3200 | Bilateral - Avarie HVDC Gde Ile-Piossasco
20231222 | 0830 | December | 9400 | 8667 | 3200 | 473 | -7690 | -7690 | -6959 | TTC Selection - LTTC | TTC Selection - LTTC | 733 | 0 | FR | 3200 | Bilateral - Avarie HVDC Gde Ile-Piossasco
20231222 | 0930 | December | 9587 | 8704 | 3200 | 477 | -1938 | -1938 | -1155 | Critical Branch | Validation phase | 883 | 0 | FR | 3200 | Bilateral - Avarie HVDC Gde Ile-Piossasco |  |  |  | CH | 9275 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231222 | 1030 | December | 9287 | 8420 | 3200 | 211 | -1666 | -1666 | -902 | Critical Branch | Validation phase | 867 | 0 | FR | 3200 | Bilateral - Avarie HVDC Gde Ile-Piossasco |  |  |  | CH | 8975 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231222 | 1130 | December | 9287 | 8420 | 3200 | 211 | -1666 | -1666 | -902 | Critical Branch | Validation phase | 867 | 0 | FR | 3200 | Bilateral - Avarie HVDC Gde Ile-Piossasco |  |  |  | CH | 8975 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231222 | 1230 | December | 9542 | 8160 | 3200 | 200 | -2308 | -2308 | -988 | Critical Branch | Validation phase | 1382 | 0 | FR | 3200 | Bilateral - Avarie HVDC Gde Ile-Piossasco |  |  |  | CH | 8499 | Missing CNEC in CC: CNE: 220kV Ponte - Y/Acqua , C: N-2 Pradella-Robbia + Filisur-Robbia
20231222 | 1330 | December | 9842 | 8438 | 3200 | 452 | -2583 | -2583 | -1240 | Critical Branch | Validation phase | 1404 | 0 | FR | 3200 | Bilateral - Avarie HVDC Gde Ile-Piossasco |  |  |  | CH | 8799 | Missing CNEC in CC: CNE: 220kV Ponte - Y/Acqua , C: N-2 Pradella-Robbia + Filisur-Robbia
20231222 | 1430 | December | 9842 | 8438 | 3200 | 452 | -2583 | -2583 | -1240 | Critical Branch | Validation phase | 1404 | 0 | FR | 3200 | Bilateral - Avarie HVDC Gde Ile-Piossasco |  |  |  | CH | 8799 | Missing CNEC in CC: CNE: 220kV Ponte - Y/Acqua , C: N-2 Pradella-Robbia + Filisur-Robbia
20231222 | 1530 | December | 9711 | 8510 | 3200 | 458 | -1816 | -1816 | -688 | Critical Branch | Validation phase | 1201 | 0 | FR | 3200 | Bilateral - Avarie HVDC Gde Ile-Piossasco |  |  |  | CH | 8928 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231222 | 1630 | December | 9711 | 8510 | 3200 | 458 | -1816 | -1816 | -688 | Critical Branch | Validation phase | 1201 | 0 | FR | 3200 | Bilateral - Avarie HVDC Gde Ile-Piossasco |  |  |  | CH | 8928 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231222 | 1730 | December | 9911 | 8697 | 3200 | 460 | -2045 | -2045 | -905 | Critical Branch | Validation phase | 1214 | 0 | FR | 3200 | Bilateral - Avarie HVDC Gde Ile-Piossasco |  |  |  | CH | 9128 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231222 | 1830 | December | 9600 | 8857 | 3200 | 475 | -2293 | -2293 | -1645 | TTC Selection - LTTC | TTC Selection - LTTC | 743 | 0 | FR | 3200 | Bilateral - Avarie HVDC Gde Ile-Piossasco
20231222 | 1930 | December | 9600 | 8857 | 3200 | 475 | -2293 | -2293 | -1645 | TTC Selection - LTTC | TTC Selection - LTTC | 743 | 0 | FR | 3200 | Bilateral - Avarie HVDC Gde Ile-Piossasco
20231222 | 2030 | December | 9600 | 8857 | 3200 | 475 | -2293 | -2293 | -1645 | TTC Selection - LTTC | TTC Selection - LTTC | 743 | 0 | FR | 3200 | Bilateral - Avarie HVDC Gde Ile-Piossasco
20231222 | 2130 | December | 9600 | 8857 | 3200 | 475 | -8621 | -8621 | -7879 | TTC Selection - LTTC | TTC Selection - LTTC | 743 | 0 | FR | 3200 | Bilateral - Avarie HVDC Gde Ile-Piossasco
20231222 | 2230 | December | 9600 | 8857 | 3200 | 475 | -8621 | -8621 | -7879 | TTC Selection - LTTC | TTC Selection - LTTC | 743 | 0 | FR | 3200 | Bilateral - Avarie HVDC Gde Ile-Piossasco
20231222 | 2330 | December | 8790 | 8220 | 3200 | 456 | -7811 | -7811 | -7243 | TTC Selection - LTTC | TTC Selection - LTTC | 570 | 0 | FR | 3200 | Bilateral - Avarie HVDC Gde Ile-Piossasco
20231226 | 0030 | December | 8890 | 8275 | 3200 | 462 | -4126 | -4126 | -3524 | TTC Selection - LTTC | TTC Selection - LTTC | 615 | 0 | FR | 3200 | Bilateral - Avarie G.Ille-Piossasco 1
20231226 | 0130 | December | 8890 | 8275 | 3200 | 462 | -4126 | -4126 | -3524 | TTC Selection - LTTC | TTC Selection - LTTC | 615 | 0 | FR | 3200 | Bilateral - Avarie G.Ille-Piossasco 1
20231226 | 0230 | December | 8890 | 8275 | 3200 | 462 | -4126 | -4126 | -3524 | TTC Selection - LTTC | TTC Selection - LTTC | 615 | 0 | FR | 3200 | Bilateral - Avarie G.Ille-Piossasco 1
20231226 | 0330 | December | 8890 | 8275 | 3200 | 462 | -3766 | -3766 | -3178 | TTC Selection - LTTC | TTC Selection - LTTC | 615 | 0 | FR | 3200 | Bilateral - Avarie G.Ille-Piossasco 1
20231226 | 0430 | December | 8890 | 8275 | 3200 | 462 | -3766 | -3766 | -3178 | TTC Selection - LTTC | TTC Selection - LTTC | 615 | 0 | FR | 3200 | Bilateral - Avarie G.Ille-Piossasco 1
20231226 | 0530 | December | 8890 | 8275 | 3200 | 462 | -3766 | -3766 | -3178 | TTC Selection - LTTC | TTC Selection - LTTC | 615 | 0 | FR | 3200 | Bilateral - Avarie G.Ille-Piossasco 1
20231226 | 0630 | December | 8890 | 8275 | 3200 | 462 | -3766 | -3766 | -3178 | TTC Selection - LTTC | TTC Selection - LTTC | 615 | 0 | FR | 3200 | Bilateral - Avarie G.Ille-Piossasco 1
20231226 | 0730 | December | 8790 | 8220 | 3200 | 456 | -7235 | -7235 | -6669 | TTC Selection - LTTC | TTC Selection - LTTC | 570 | 0 | FR | 3200 | Bilateral - Avarie G.Ille-Piossasco 1
20231226 | 0830 | December | 8790 | 8220 | 3200 | 456 | -7235 | -7235 | -6669 | TTC Selection - LTTC | TTC Selection - LTTC | 570 | 0 | FR | 3200 | Bilateral - Avarie G.Ille-Piossasco 1
20231226 | 0930 | December | 9073 | 8375 | 3200 | 472 | -3559 | -3559 | -2929 | Critical Branch | Critical Branch | 698 | 0 | FR | 3200 | Bilateral - Avarie G.Ille-Piossasco 1
20231226 | 1030 | December | 9073 | 8375 | 3200 | 472 | -3559 | -3559 | -2929 | Critical Branch | Critical Branch | 698 | 0 | FR | 3200 | Bilateral - Avarie G.Ille-Piossasco 1
20231226 | 1130 | December | 9073 | 8375 | 3200 | 472 | -3559 | -3559 | -2929 | Critical Branch | Critical Branch | 698 | 0 | FR | 3200 | Bilateral - Avarie G.Ille-Piossasco 1
20231226 | 1230 | December | 9255 | 8474 | 3200 | 482 | -3967 | -3967 | -3258 | Critical Branch | Critical Branch | 781 | 0 | FR | 3200 | Bilateral - Avarie G.Ille-Piossasco 1
20231226 | 1330 | December | 9255 | 8474 | 3200 | 482 | -3967 | -3967 | -3258 | Critical Branch | Critical Branch | 781 | 0 | FR | 3200 | Bilateral - Avarie G.Ille-Piossasco 1
20231226 | 1430 | December | 9255 | 8474 | 3200 | 482 | -3967 | -3967 | -3258 | Critical Branch | Critical Branch | 781 | 0 | FR | 3200 | Bilateral - Avarie G.Ille-Piossasco 1
20231226 | 1530 | December | 8790 | 8220 | 3200 | 456 | -5552 | -5552 | -4996 | TTC Selection - LTTC | TTC Selection - LTTC | 570 | 0 | FR | 3200 | Bilateral - Avarie G.Ille-Piossasco 1
20231226 | 1630 | December | 8790 | 8220 | 3200 | 456 | -5552 | -5552 | -4996 | TTC Selection - LTTC | TTC Selection - LTTC | 570 | 0 | FR | 3200 | Bilateral - Avarie G.Ille-Piossasco 1
20231226 | 1730 | December | 8790 | 8220 | 3200 | 456 | -5552 | -5552 | -4996 | TTC Selection - LTTC | TTC Selection - LTTC | 570 | 0 | FR | 3200 | Bilateral - Avarie G.Ille-Piossasco 1
20231226 | 1830 | December | 8957 | 8311 | 3200 | 465 | -3073 | -3073 | -2497 | Critical Branch | Critical Branch | 646 | 0 | FR | 3200 | Bilateral - Avarie G.Ille-Piossasco 1
20231226 | 1930 | December | 8957 | 8311 | 3200 | 465 | -3073 | -3073 | -2497 | Critical Branch | Critical Branch | 646 | 0 | FR | 3200 | Bilateral - Avarie G.Ille-Piossasco 1
20231226 | 2030 | December | 8957 | 8311 | 3200 | 465 | -3073 | -3073 | -2497 | Critical Branch | Critical Branch | 646 | 0 | FR | 3200 | Bilateral - Avarie G.Ille-Piossasco 1
20231226 | 2130 | December | 8790 | 8220 | 3200 | 456 | -6554 | -6554 | -5994 | TTC Selection - LTTC | TTC Selection - LTTC | 570 | 0 | FR | 3200 | Bilateral - Avarie G.Ille-Piossasco 1
20231226 | 2230 | December | 8790 | 8220 | 3200 | 456 | -6554 | -6554 | -5994 | TTC Selection - LTTC | TTC Selection - LTTC | 570 | 0 | FR | 3200 | Bilateral - Avarie G.Ille-Piossasco 1
20231226 | 2330 | December | 8790 | 8220 | 3200 | 456 | -6554 | -6554 | -5994 | TTC Selection - LTTC | TTC Selection - LTTC | 570 | 0 | FR | 3200 | Bilateral - Avarie G.Ille-Piossasco 1
20231227 | 0030 | December | 8890 | 8275 | 3200 | 462 | -2717 | -2717 | -2135 | TTC Selection - LTTC | TTC Selection - LTTC | 615 | 0 | FR | 3200 | Bilateral - Avarie G.Ile-Piossasco 1
20231227 | 0130 | December | 8890 | 8275 | 3200 | 462 | -2717 | -2717 | -2135 | TTC Selection - LTTC | TTC Selection - LTTC | 615 | 0 | FR | 3200 | Bilateral - Avarie G.Ile-Piossasco 1
20231227 | 0230 | December | 8890 | 8275 | 3200 | 462 | -2717 | -2717 | -2135 | TTC Selection - LTTC | TTC Selection - LTTC | 615 | 0 | FR | 3200 | Bilateral - Avarie G.Ile-Piossasco 1
20231227 | 0330 | December | 9283 | 8489 | 3200 | 483 | -2692 | -2692 | -1941 | Critical Branch | Critical Branch | 794 | 0 | FR | 3200 | Bilateral - Avarie G.Ile-Piossasco 1
20231227 | 0430 | December | 9283 | 8489 | 3200 | 483 | -2692 | -2692 | -1941 | Critical Branch | Critical Branch | 794 | 0 | FR | 3200 | Bilateral - Avarie G.Ile-Piossasco 1
20231227 | 0530 | December | 9283 | 8489 | 3200 | 483 | -2692 | -2692 | -1941 | Critical Branch | Critical Branch | 794 | 0 | FR | 3200 | Bilateral - Avarie G.Ile-Piossasco 1
20231227 | 0630 | December | 9283 | 8489 | 3200 | 483 | -2692 | -2692 | -1941 | Critical Branch | Critical Branch | 794 | 0 | FR | 3200 | Bilateral - Avarie G.Ile-Piossasco 1
20231227 | 0730 | December | 9600 | 8857 | 3200 | 475 | -2223 | -2223 | -1520 | TTC Selection - LTTC | TTC Selection - LTTC | 743 | 0 | FR | 3200 | Bilateral - Avarie G.Ile-Piossasco 1
20231227 | 0830 | December | 9600 | 8857 | 3200 | 475 | -2223 | -2223 | -1520 | TTC Selection - LTTC | TTC Selection - LTTC | 743 | 0 | FR | 3200 | Bilateral - Avarie G.Ile-Piossasco 1
20231227 | 0930 | December | 9600 | 8857 | 3200 | 475 | -1863 | -1863 | -1159 | TTC Selection - LTTC | TTC Selection - LTTC | 743 | 0 | FR | 3200 | Bilateral - Avarie G.Ile-Piossasco 1
20231227 | 1030 | December | 9600 | 8857 | 3200 | 475 | -1863 | -1863 | -1159 | TTC Selection - LTTC | TTC Selection - LTTC | 743 | 0 | FR | 3200 | Bilateral - Avarie G.Ile-Piossasco 1
20231227 | 1130 | December | 9600 | 8857 | 3200 | 475 | -1863 | -1863 | -1159 | TTC Selection - LTTC | TTC Selection - LTTC | 743 | 0 | FR | 3200 | Bilateral - Avarie G.Ile-Piossasco 1
20231227 | 1230 | December | 9600 | 8857 | 3200 | 475 | -2244 | -2244 | -1526 | TTC Selection - LTTC | TTC Selection - LTTC | 743 | 0 | FR | 3200 | Bilateral - Avarie G.Ile-Piossasco 1
20231227 | 1330 | December | 9600 | 8857 | 3200 | 475 | -2244 | -2244 | -1526 | TTC Selection - LTTC | TTC Selection - LTTC | 743 | 0 | FR | 3200 | Bilateral - Avarie G.Ile-Piossasco 1
20231227 | 1430 | December | 9600 | 8857 | 3200 | 475 | -2244 | -2244 | -1526 | TTC Selection - LTTC | TTC Selection - LTTC | 743 | 0 | FR | 3200 | Bilateral - Avarie G.Ile-Piossasco 1
20231227 | 1530 | December | 9893 | 9023 | 3200 | 490 | -2010 | -2010 | -1183 | Critical Branch | Critical Branch | 870 | 0 | FR | 3200 | Bilateral - Avarie G.Ile-Piossasco 1
20231227 | 1630 | December | 9893 | 9023 | 3200 | 490 | -2010 | -2010 | -1183 | Critical Branch | Critical Branch | 870 | 0 | FR | 3200 | Bilateral - Avarie G.Ile-Piossasco 1
20231227 | 1730 | December | 9893 | 9023 | 3200 | 490 | -2010 | -2010 | -1183 | Critical Branch | Critical Branch | 870 | 0 | FR | 3200 | Bilateral - Avarie G.Ile-Piossasco 1
20231227 | 1830 | December | 10080 | 9129 | 3200 | 500 | -2688 | -2688 | -1776 | Critical Branch | Critical Branch | 951 | 0 | FR | 3200 | Bilateral - Avarie G.Ile-Piossasco 1
20231227 | 1930 | December | 10080 | 9129 | 3200 | 500 | -2688 | -2688 | -1776 | Critical Branch | Critical Branch | 951 | 0 | FR | 3200 | Bilateral - Avarie G.Ile-Piossasco 1
20231227 | 2030 | December | 10080 | 9129 | 3200 | 500 | -2688 | -2688 | -1776 | Critical Branch | Critical Branch | 951 | 0 | FR | 3200 | Bilateral - Avarie G.Ile-Piossasco 1
20231227 | 2130 | December | 9600 | 8857 | 3200 | 475 | -3182 | -3182 | -2487 | TTC Selection - LTTC | TTC Selection - LTTC | 743 | 0 | FR | 3200 | Bilateral - Avarie G.Ile-Piossasco 1
20231227 | 2230 | December | 9600 | 8857 | 3200 | 475 | -3182 | -3182 | -2487 | TTC Selection - LTTC | TTC Selection - LTTC | 743 | 0 | FR | 3200 | Bilateral - Avarie G.Ile-Piossasco 1
20231227 | 2330 | December | 8790 | 8220 | 3200 | 456 | -2356 | -2356 | -1825 | TTC Selection - LTTC | TTC Selection - LTTC | 570 | 0 | FR | 3200 | Bilateral - Avarie G.Ile-Piossasco 1
20231228 | 0030 | December | 8890 | 8275 | 3200 | 462 | -6819 | -6819 | -6225 | TTC Selection - LTTC | TTC Selection - LTTC | 615 | 0 | FR | 3200 | Bilateral - Avarie G.ILE PIOSSASCO 1
20231228 | 0130 | December | 8890 | 8275 | 3200 | 462 | -6819 | -6819 | -6225 | TTC Selection - LTTC | TTC Selection - LTTC | 615 | 0 | FR | 3200 | Bilateral - Avarie G.ILE PIOSSASCO 1
20231228 | 0230 | December | 8890 | 8275 | 3200 | 462 | -6819 | -6819 | -6225 | TTC Selection - LTTC | TTC Selection - LTTC | 615 | 0 | FR | 3200 | Bilateral - Avarie G.ILE PIOSSASCO 1
20231228 | 0330 | December | 8890 | 8275 | 3200 | 462 | -5896 | -5896 | -5311 | TTC Selection - LTTC | TTC Selection - LTTC | 615 | 0 | FR | 3200 | Bilateral - Avarie G.ILE PIOSSASCO 1
20231228 | 0430 | December | 8890 | 8275 | 3200 | 462 | -5896 | -5896 | -5311 | TTC Selection - LTTC | TTC Selection - LTTC | 615 | 0 | FR | 3200 | Bilateral - Avarie G.ILE PIOSSASCO 1
20231228 | 0530 | December | 8890 | 8275 | 3200 | 462 | -5896 | -5896 | -5311 | TTC Selection - LTTC | TTC Selection - LTTC | 615 | 0 | FR | 3200 | Bilateral - Avarie G.ILE PIOSSASCO 1
20231228 | 0630 | December | 8890 | 8275 | 3200 | 462 | -5896 | -5896 | -5311 | TTC Selection - LTTC | TTC Selection - LTTC | 615 | 0 | FR | 3200 | Bilateral - Avarie G.ILE PIOSSASCO 1
20231228 | 0730 | December | 9600 | 8857 | 3200 | 475 | -4952 | -4952 | -4265 | TTC Selection - LTTC | TTC Selection - LTTC | 743 | 0 | FR | 3200 | Bilateral - Avarie G.ILE PIOSSASCO 1
20231228 | 0830 | December | 9600 | 8857 | 3200 | 475 | -4952 | -4952 | -4265 | TTC Selection - LTTC | TTC Selection - LTTC | 743 | 0 | FR | 3200 | Bilateral - Avarie G.ILE PIOSSASCO 1
20231228 | 0930 | December | 9600 | 8857 | 3200 | 475 | -7250 | -7250 | -6532 | TTC Selection - LTTC | TTC Selection - LTTC | 743 | 0 | FR | 3200 | Bilateral - Avarie G.ILE PIOSSASCO 1
20231228 | 1030 | December | 9600 | 8857 | 3200 | 475 | -7250 | -7250 | -6532 | TTC Selection - LTTC | TTC Selection - LTTC | 743 | 0 | FR | 3200 | Bilateral - Avarie G.ILE PIOSSASCO 1
20231228 | 1130 | December | 9600 | 8857 | 3200 | 475 | -7250 | -7250 | -6532 | TTC Selection - LTTC | TTC Selection - LTTC | 743 | 0 | FR | 3200 | Bilateral - Avarie G.ILE PIOSSASCO 1
20231228 | 1230 | December | 9600 | 8857 | 3200 | 475 | -4787 | -4787 | -4099 | TTC Selection - LTTC | TTC Selection - LTTC | 743 | 0 | FR | 3200 | Bilateral - Avarie G.ILE PIOSSASCO 1
20231228 | 1330 | December | 9600 | 8857 | 3200 | 475 | -4787 | -4787 | -4099 | TTC Selection - LTTC | TTC Selection - LTTC | 743 | 0 | FR | 3200 | Bilateral - Avarie G.ILE PIOSSASCO 1
20231228 | 1430 | December | 9600 | 8857 | 3200 | 475 | -4787 | -4787 | -4099 | TTC Selection - LTTC | TTC Selection - LTTC | 743 | 0 | FR | 3200 | Bilateral - Avarie G.ILE PIOSSASCO 1
20231228 | 1530 | December | 9600 | 8857 | 3200 | 475 | -5845 | -5845 | -5106 | TTC Selection - LTTC | TTC Selection - LTTC | 743 | 0 | FR | 3200 | Bilateral - Avarie G.ILE PIOSSASCO 1
20231228 | 1630 | December | 9600 | 8857 | 3200 | 475 | -5845 | -5845 | -5106 | TTC Selection - LTTC | TTC Selection - LTTC | 743 | 0 | FR | 3200 | Bilateral - Avarie G.ILE PIOSSASCO 1
20231228 | 1730 | December | 9600 | 8857 | 3200 | 475 | -5845 | -5845 | -5106 | TTC Selection - LTTC | TTC Selection - LTTC | 743 | 0 | FR | 3200 | Bilateral - Avarie G.ILE PIOSSASCO 1
20231228 | 1830 | December | 9600 | 8857 | 3200 | 475 | -6664 | -6664 | -5929 | TTC Selection - LTTC | TTC Selection - LTTC | 743 | 0 | FR | 3200 | Bilateral - Avarie G.ILE PIOSSASCO 1
20231228 | 1930 | December | 9600 | 8857 | 3200 | 475 | -6664 | -6664 | -5929 | TTC Selection - LTTC | TTC Selection - LTTC | 743 | 0 | FR | 3200 | Bilateral - Avarie G.ILE PIOSSASCO 1
20231228 | 2030 | December | 9600 | 8857 | 3200 | 475 | -6664 | -6664 | -5929 | TTC Selection - LTTC | TTC Selection - LTTC | 743 | 0 | FR | 3200 | Bilateral - Avarie G.ILE PIOSSASCO 1
20231228 | 2130 | December | 9600 | 8857 | 3200 | 475 | -3464 | -3464 | -2751 | TTC Selection - LTTC | TTC Selection - LTTC | 743 | 0 | FR | 3200 | Bilateral - Avarie G.ILE PIOSSASCO 1
20231228 | 2230 | December | 9600 | 8857 | 3200 | 475 | -3464 | -3464 | -2751 | TTC Selection - LTTC | TTC Selection - LTTC | 743 | 0 | FR | 3200 | Bilateral - Avarie G.ILE PIOSSASCO 1
20231228 | 2330 | December | 8790 | 8220 | 3200 | 456 | -2646 | -2646 | -2100 | TTC Selection - LTTC | TTC Selection - LTTC | 570 | 0 | FR | 3200 | Bilateral - Avarie G.ILE PIOSSASCO 1

## D2 FLAGS processing
TSO | Long description | Short | Type | # of TS
AT | Bilateral - Reduction because NTC over thermal limit on border | Bilateral - Reduction because NTC over thermal limit on border | Overload | 105
FR | Bilateral - RDCR CREY ST VULBAS 2 | Bilateral - RDCR CREY ST VULBAS 2 | Fault | 17
CH | Missing CNEC in CC: CNE: 380kV Gorlago - Robbia , C: N-2 ALBERTVILLE-RONDISSONE | CNE: 380kV Gorlago - Robbia , C: N-2 ALBERTVILLE-RONDISSONE | Missing CNEC | 3
CH | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | IT issues in internal Validation Tool. BackUp-NTC-values are applied. | IT Issues | 32
CH | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 ALBERTVILLE-RONDISSONE | CNE: 380kV Lavorgo - Musignano , C: N-2 ALBERTVILLE-RONDISSONE | Overload | 3
CH | Expected overloading on the following CNEC: CNE: 380kV Gorlago - Robbia , C: N-1 SOAZZA-BULCIAGO | CNE: 380kV Gorlago - Robbia , C: N-1 SOAZZA-BULCIAGO | Overload | 6
CH | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE | CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE | Missing CNEC | 46
FR | Bilateral - Problèmes de coordination avec TERNA | Bilateral - Problèmes de coordination avec TERNA | Coordination problem | 18
FR | Bilateral - N-2 ALBERTVILLE-RONDISSONE/ALBERTVILLE G.ILE 3 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/ALBERTVILLE G.ILE 3 | Fault | 20
FR | Bilateral - N-2 ALBERTVILLE-RONDISSONE/ALBERTVILLE-G.ILE 3 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/ALBERTVILLE-G.ILE 3 | Fault | 21
FR | Bilateral - Problème Coordination TERNA | Bilateral - Problème Coordination TERNA | Coordination problem | 46
FR | Bilateral - Red Flag RTE | Bilateral - Red Flag RTE | Not Specified | 7
CH | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE | CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE | Overload | 21
CH | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Pradella-Robbia + Filisur-Robbia | CNE: 380kV Bulciago - Soazza , C: N-2 Pradella-Robbia + Filisur-Robbia | Overload | 11
FR | Bilateral - N-2 ALBERTVILLE GRANDE ILE | Bilateral - N-2 ALBERTVILLE GRANDE ILE | Fault | 24
FR | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT | Fault | 69
FR | Bilateral - N-2 ALBERTVILLE - RONDISSONE | Bilateral - N-2 ALBERTVILLE - RONDISSONE | Fault | 24
FR | Bilateral - N-2 Albertville Rondissone / Albertvillee-Grande Ile | Bilateral - N-2 Albertville Rondissone / Albertvillee-Grande Ile | Fault | 24
FR | Bilateral - N-2 Alberville-Rondissonne / Cornier Riddes | Bilateral - N-2 Alberville-Rondissonne / Cornier Riddes | Fault | 16
FR | Bilateral - N-2 Alberville-Rondissonne / Cornier-Riddes | Bilateral - N-2 Alberville-Rondissonne / Cornier-Riddes | Fault | 1
IT | N-1 ABV-RON2 -> ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid, | N-1 ABV-RON2 -> ABV -GRA 3 and viceversa, N-1 RON-ABV1 on RON-ABV 2 and viceversa, N-2 ABV - RON on 220 kV CH-IT grid, | Fault | 22
CH | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | Overload | 89
IT | ABV-GRA1/2 -&gt; ABV-GRA3, ABV-RON1 on ABV-RON2 and viceversa | ABV-GRA1/2 -&gt; ABV-GRA3, ABV-RON1 on ABV-RON2 and viceversa | Fault | 4
IT | N-2 ABV - RON on 220 kV grid | N-2 ABV - RON on 220 kV grid | Fault | 7
IT | ABV-GRA1-2 on ABV-GRA 3 and ABV-RON 1-2 on VNS-VLR | ABV-GRA1-2 on ABV-GRA 3 and ABV-RON 1-2 on VNS-VLR | Fault | 31
FR | Bilateral - NTC Secure due to Process fail during TSO validation phase | Bilateral - NTC Secure due to Process fail during TSO validation phase | Process Fail | 7
CH | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | CNE: 380kV Lavorgo - Musignano , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | Overload | 6
IT | Expected overloading on the following CNEC: CNE: 380kV Lavorgo-Musignano, C: N-1 Soazza-Bulciago | CNE: 380kV Lavorgo-Musignano, C: N-1 Soazza-Bulciago | Overload | 22
IT | Correct value IT issue | Correct value IT issue | IT Issues | 3
IT | Computation Failed | Computation Failed | Process Fail | 3
CH | Lavorgo-Musignano N-2 Robbia-Gorlago + Robbia-S.Fiorano | Lavorgo-Musignano N-2 Robbia-Gorlago + Robbia-S.Fiorano | Fault | 3
AT | Bilateral - Reduction because of outage of line 912 | Bilateral - Reduction because of outage of line 912 | Fault | 25
IT | N-1 ABV-RON1 ->ABV-RON2 | N-1 ABV-RON1 ->ABV-RON2 | Fault | 2
IT | N-1 ABV-RON1 -&gt;ABV-RON2 | N-1 ABV-RON1 -&gt;ABV-RON2 | Fault | 10
IT | N-2 ROB-SFI/GOR-ROB on BUL-SOA | N-2 ROB-SFI/GOR-ROB on BUL-SOA | Fault | 3
FR | Bilateral - CREYS GENISSIAT | Bilateral - CREYS GENISSIAT | Fault | 13
IT | safe value | safe value | Not Specified | 20
FR | Bilateral - RDCR CREYS GENISSIAT N°1 | Bilateral - RDCR CREYS GENISSIAT N°1 | Fault | 24
FR | Bilateral - RDCR CORNIER GENISSIAT | Bilateral - RDCR CORNIER GENISSIAT | Fault | 7
IT | N-2 380 kV ABV-RON 1&2 -> 380 kV PRA-VLR | N-2 380 kV ABV-RON 1&2 -> 380 kV PRA-VLR | Not Specified | 1
IT | N-2 380 kV ABV-RON 1&amp;2 -&gt; 380 kV PRA-VLR | N-2 380 kV ABV-RON 1&amp;2 -&gt; 380 kV PRA-VLR | Fault | 2
IT | N-2 380 kV ABV-GRA1&amp;2 -&gt; 380 kV ABV-GRA3 | N-2 380 kV ABV-GRA1&amp;2 -&gt; 380 kV ABV-GRA3 | Fault | 2
IT | N-2 380 kV ABV-GRA1&2 -> 380 kV ABV-GRA3 | N-2 380 kV ABV-GRA1&2 -> 380 kV ABV-GRA3 | Fault | 1
IT | N-2 380 kV ABV-GRA1&amp;amp;2 -&amp;gt; 380 kV ABV-GRA3 | N-2 380 kV ABV-GRA1&amp;amp;2 -&amp;gt; 380 kV ABV-GRA3 | Fault | 4
CH | Same value as the two other hours | Same value as the two other hours | Not Specified | 1
FR | Bilateral - Echec du calcul reprise NTC de 11h30 | Bilateral - Echec du calcul reprise NTC de 11h30 | Process Fail | 3
FR | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT | Fault | 48
FR | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT 2 | Bilateral - N-2 ALBERTVILLE-G.ILE/CREYS-GENISSIAT 2 | Fault | 23
IT | CO Value | CO Value | Not Specified | 9
FR | Bilateral - RDCR CREYS - GENISSIAT 1 | Bilateral - RDCR CREYS - GENISSIAT 1 | Fault | 58
FR | Bilateral - RDCR CREYS-GENISSIAT 1 | Bilateral - RDCR CREYS-GENISSIAT 1 | Fault | 21
FR | Bilateral - retrait CREYS GENISSIAT 1 | Bilateral - retrait CREYS GENISSIAT 1 | Fault | 24
FR | Bilateral - Retrait Creys Génissiat 1 | Bilateral - Retrait Creys Génissiat 1 | Fault | 15
FR | Bilateral - Retrait Creys Génissiat 1 + essai HVDC FR IT | Bilateral - Retrait Creys Génissiat 1 + essai HVDC FR IT | Fault | 9
FR | Bilateral - RDCR CREYS GENISSIAT 1 | Bilateral - RDCR CREYS GENISSIAT 1 | Fault | 18
FR | Bilateral - RACR CREYS GENISSIAT 1 | Bilateral - RACR CREYS GENISSIAT 1 | Fault | 6
FR | Bilateral - RDCR VENAUS - VILLARODIN | Bilateral - RDCR VENAUS - VILLARODIN | Fault | 1
IT | ABV-GRA 1-2 on ABV-GRA 3, RON-ABV1 on RON-ABV2 and ABV-RON1-2 on VNS-VLR | ABV-GRA 1-2 on ABV-GRA 3, RON-ABV1 on RON-ABV2 and ABV-RON1-2 on VNS-VLR | Fault | 32
FR | Bilateral - Essais FIL | Bilateral - Essais FIL | Fault | 1
IT | N-2 ABV-RON1&2 on VNS-VLR(101%) | N-2 ABV-RON1&2 on VNS-VLR(101%) | Fault | 1
IT | N-2 ABV-RON1&amp;2 on VNS-VLR(101%) | N-2 ABV-RON1&amp;2 on VNS-VLR(101%) | Fault | 13
IT | N-1 380 kV ROB-GOR&ROB-SFI -> 380kV SIL-SOA | N-1 380 kV ROB-GOR&ROB-SFI -> 380kV SIL-SOA | Fault | 1
IT | N-1 380 kV ROB-GOR&amp;ROB-SFI -&gt; 380kV SIL-SOA | N-1 380 kV ROB-GOR&amp;ROB-SFI -&gt; 380kV SIL-SOA | Fault | 4
IT | N-1 380 kV ROB-GOR&amp;amp;ROB-SFI -&amp;gt; 380kV SIL-SOA | N-1 380 kV ROB-GOR&amp;amp;ROB-SFI -&amp;gt; 380kV SIL-SOA | Fault | 3
FR | Bilateral - Avarie HVDC Gde Ile-Piossasco | Bilateral - Avarie HVDC Gde Ile-Piossasco | Fault | 24
FR | Bilateral - Avarie G.Ille-Piossasco 1 | Bilateral - Avarie G.Ille-Piossasco 1 | Fault | 24
FR | Bilateral - Avarie G.Ile-Piossasco 1 | Bilateral - Avarie G.Ile-Piossasco 1 | Fault | 24
FR | Bilateral - Avarie G.ILE PIOSSASCO 1 | Bilateral - Avarie G.ILE PIOSSASCO 1 | Fault | 24

## ID 70% reduction
ID 70% reduction results
|  |  | TTC (MW) | ANTC (MW) |  | LimitedBy | Reduction
BD | Month | TS | Adjustment | ANTCfinal | ANTCfeasible | Adjustment | 70% Reduction (MW) | % reduction | Category
20231119 | November | 1830 | 9435 | 2902 | 483 | Minimum Margin | 2419 | 83.36% | above 1000 MW
20231119 | November | 1930 | 9435 | 2902 | 483 | Minimum Margin | 2419 | 83.36% | above 1000 MW
20231119 | November | 2030 | 9435 | 2902 | 483 | Minimum Margin | 2419 | 83.36% | above 1000 MW
20231219 | December | 1230 | 10377 | 433 | 238 | Minimum Margin | 195 | 45.03% | below 500 MW
20231219 | December | 1330 | 10377 | 433 | 238 | Minimum Margin | 195 | 45.03% | below 500 MW
20231219 | December | 1430 | 10377 | 433 | 238 | Minimum Margin | 195 | 45.03% | below 500 MW

## ID validation reduction
ID Validation reduction results
|  |  | TTC Adjustment |  |  | TTC Validation |  |  | NTC-Import | NTC-Export | ANTC |  |  | LimitedBy |  | Individual Validation Reduction |  |  | Limiting Flags
BD | Month | TS | TTC_Import | TTC_Transit_Import | TTC_Transit_Export | TTC_Import | TTC_Transit_Import | TTC_Transit_Export | AT-IT FR-IT | IT-AT IT-FR | Final | Feasible | NTC1 | Adj | NTC1 | TTC Reduction - Import | TTC Reduction - Transit | Reduction TTC and 70% | TSO | MNII MIEC | Reason | TSO | MNII MIEC | Reason | TSO | MNII MIEC | Reason
20231001 | October | 2030 | 8978 |  |  | 7415 |  |  |  |  | -3113 | -3113 | -1554 | Critical Branch | Validation phase | 1563 | NA | 0 | CH | 7140 | Expected overloading on the following CNEC: CNE: 380kV Gorlago - Robbia , C: N-1 SOAZZA-BULCIAGO
20231001 | October | 2130 | 9484 |  |  | 7342 |  |  |  |  | -2981 | -2981 | -851 | Critical Branch | Validation phase | 2142 | NA | 0 | CH | 7062 | Expected overloading on the following CNEC: CNE: 380kV Gorlago - Robbia , C: N-1 SOAZZA-BULCIAGO
20231002 | October | 1530 | 9257 |  |  | 8552 |  |  |  |  | -5212 | -5212 | -4507 | Critical Branch | Validation phase | 705 | NA | 0 | CH | 8362 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231002 | October | 1630 | 9257 |  |  | 8229 |  |  |  |  | -5212 | -5212 | -4184 | Critical Branch | Validation phase | 1028 | NA | 0 | CH | 8039 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231002 | October | 1730 | 9257 |  |  | 7272 |  |  |  |  | -5212 | -5212 | -3512 | Critical Branch | Validation phase | 1985 | NA | 0 | CH | 7082 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231002 | October | 2130 | 9131 |  |  | 7604 |  |  |  |  | -3590 | -3590 | -1925 | Critical Branch | Validation phase | 1527 | NA | 0 | CH | 7410 | Expected overloading on the following CNEC: CNE: 380kV Gorlago - Robbia , C: N-1 SOAZZA-BULCIAGO
20231002 | October | 2230 | 9131 |  |  | 7945 |  |  |  |  | -3590 | -3590 | -2344 | Critical Branch | Validation phase | 1186 | NA | 0 | CH | 7755 | Expected overloading on the following CNEC: CNE: 380kV Gorlago - Robbia , C: N-1 SOAZZA-BULCIAGO
20231002 | October | 2330 | 8336 |  |  | 8331 |  |  | AT-IT = 0 |  | -2758 | -2758 | -2755 | Critical Branch | TTC Validation phase - bilateral reduction | 5 | NA | 0 | AT | 0 | Bilateral - Reduction because of disconnection of line 261 & 912
20231004 | October | 1430 | 8210 |  |  | 8125 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 85 | NA | 0 | CH | 7935 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 ALBERTVILLE-RONDISSONE
20231004 | October | 2030 | 8121 |  |  | 7977 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 144 | NA | 0 | CH | 7787 | Expected overloading on the following CNEC: CNE: 380kV Gorlago - Robbia , C: N-1 SOAZZA-BULCIAGO
20231004 | October | 2130 | 7871 |  |  | 7870 |  |  | AT-IT = 0 |  | 0 | 0 | 0 | Critical Branch | Critical Branch | 1 | NA | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231004 | October | 2230 | 7871 |  |  | 7870 |  |  | AT-IT = 0 |  | 0 | 0 | 0 | Critical Branch | Critical Branch | 1 | NA | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231004 | October | 2330 | 7076 |  |  | 7071 |  |  | AT-IT = 0 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 5 | NA | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231005 | October | 1230 | 8210 |  |  | 8170 |  |  | AT-IT = 0 |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 40 | NA | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231005 | October | 1330 | 8210 |  |  | 8170 |  |  | AT-IT = 0 |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 40 | NA | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231005 | October | 1730 | 8210 |  |  | 8202 |  |  | AT-IT = 0 |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 8 | NA | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231005 | October | 1830 | 8210 |  |  | 8162 |  |  | AT-IT = 0 |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 48 | NA | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231005 | October | 1930 | 8210 |  |  | 8162 |  |  | AT-IT = 0 |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 48 | NA | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231005 | October | 2030 | 8210 |  |  | 8202 |  |  | AT-IT = 0 |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 8 | NA | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231006 | October | 1230 | 7701 |  |  | 7300 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 401 | NA | 0 | CH | 7025 | Reduction due to the following overloaded element(s): N-2 380kV Pradella-Robbia + Filisur-Robbia : 380kV Sils-Soazza
20231006 | October | 1330 | 7701 |  |  | 7300 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 401 | NA | 0 | CH | 7025 | Reduction due to the following overloaded element(s): N-2 380kV Pradella-Robbia + Filisur-Robbia : 380kV Sils-Soazza
20231006 | October | 1430 | 7701 |  |  | 7300 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 401 | NA | 0 | CH | 7025 | Reduction due to the following overloaded element(s): N-2 380kV Pradella-Robbia + Filisur-Robbia : 380kV Sils-Soazza
20231006 | October | 1530 | 8488 |  |  | 7500 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 988 | NA | 0 | CH | 7225 | Reduction due to the following overloaded element(s): N-2 380kV Albertville-Rondissone 1 + 2 : 220kV Avise-Riddes
20231006 | October | 1630 | 8488 |  |  | 7701 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 787 | NA | 0 | CH | 7425 | Reduction due to the following overloaded element(s): N-2 380kV Albertville-Rondissone 1 + 2 : 220kV Avise-Riddes
20231006 | October | 1730 | 8488 |  |  | 7980 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 508 | NA | 0 | CH | 7705 | Reduction due to the following overloaded element(s): N-2 380kV Albertville-Rondissone 1 + 2 : 220kV Avise-Riddes
20231007 | October | 1430 | 6130 |  |  | 6123 |  |  | AT-IT = 0 |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 7 | NA | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231007 | October | 1530 | 7848 |  |  | 7763 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Smoothing ramp | 85 | NA | 0 | Smoothing
20231007 | October | 1630 | 7848 |  |  | 7763 |  |  | AT-IT = 0 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 85 | NA | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231007 | October | 1730 | 7848 |  |  | 7763 |  |  | AT-IT = 0 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 85 | NA | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231007 | October | 1830 | 7699 |  |  | 7614 |  |  | AT-IT = 0 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 85 | NA | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231007 | October | 1930 | 7699 |  |  | 7614 |  |  | AT-IT = 0 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 85 | NA | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231007 | October | 2030 | 7699 |  |  | 7614 |  |  | AT-IT = 0 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 85 | NA | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231007 | October | 2130 | 7940 |  |  | 7847 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 93 | NA | 0 | CH | 7657 | Expected overloading on the following CNEC: CNE: 380kV Gorlago - Robbia , C: N-1 SOAZZA-BULCIAGO
20231007 | October | 2230 | 7940 |  |  | 7855 |  |  | AT-IT = 0 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 85 | NA | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231008 | October | 1830 | 8446 |  |  | 8270 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 176 | NA | 0 | CH | 8080 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231008 | October | 1930 | 8446 |  |  | 8405 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 41 | NA | 0 | CH | 8215 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231008 | October | 2330 | 8098 |  |  | 8092 |  |  | AT-IT = 0 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 6 | NA | 0 | AT | 0 | Bilateral - Reduction because NTC over thermal limit on border
20231009 | October | 1230 | 8381 |  |  | 8056 |  |  |  |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 325 | NA | 0 | AT | 0 | Reduction because NTC over thermal limit on border | FR | 1550 | N-2 ALBERVILLE RONDISSONE/ VENAUS VILLARODIN
20231009 | October | 1330 | 8381 |  |  | 7928 |  |  |  |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 453 | NA | 0 | AT | 0 | Reduction because NTC over thermal limit on border | FR | 1550 | N-2 ALBERVILLE RONDISSONE/ VENAUS VILLARODIN
20231009 | October | 1430 | 8381 |  |  | 8035 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Smoothing ramp | 346 | NA | 0 | Smoothing
20231009 | October | 1830 | 6793 |  |  | 6511 |  |  |  |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 282 | NA | 0 | AT | 0 | Reduction because NTC over thermal limit on border | FR | 1550 | N-2 ALBERVILLE RONDISSONE/ VENAUS VILLARODIN
20231009 | October | 1930 | 6793 |  |  | 5506 |  |  |  |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1287 | NA | 0 | AT | 0 | Reduction because NTC over thermal limit on border | FR | 1550 | N-2 ALBERVILLE RONDISSONE/ VENAUS VILLARODIN
20231009 | October | 2130 | 7818 |  |  | 7549 |  |  |  |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 269 | NA | 0 | AT | 0 | Reduction because NTC over thermal limit on border | FR | 1550 | N-2 ALBERVILLE RONDISSONE/ VENAUS VILLARODIN
20231009 | October | 2230 | 7818 |  |  | 6599 |  |  |  |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1219 | NA | 0 | AT | 0 | Reduction because NTC over thermal limit on border | FR | 1550 | N-2 ALBERVILLE RONDISSONE/ VENAUS VILLARODIN
20231009 | October | 2330 | 7023 |  |  | 6751 |  |  |  |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 272 | NA | 0 | AT | 0 | Reduction because NTC over thermal limit on border | FR | 1550 | N-2 ALBERVILLE RONDISSONE/ VENAUS VILLARODIN
20231010 | October | 1230 | 7642 |  |  | 7029 |  |  |  |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 613 | NA | 0 | AT | 0 | Reduction because NTC over thermal limit on border | FR | 2600 | probleme coordination avec TERNA
20231010 | October | 1330 | 7642 |  |  | 7029 |  |  |  |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 613 | NA | 0 | AT | 0 | Reduction because NTC over thermal limit on border | FR | 2600 | probleme coordination avec TERNA
20231010 | October | 1430 | 7642 |  |  | 7029 |  |  |  |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 613 | NA | 0 | AT | 0 | Reduction because NTC over thermal limit on border | FR | 2600 | probleme coordination avec TERNA
20231010 | October | 1530 | 7861 |  |  | 7150 |  |  |  |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 711 | NA | 0 | AT | 0 | Reduction because NTC over thermal limit on border | FR | 2600 | probleme coordination avec TERNA
20231010 | October | 1630 | 7861 |  |  | 7096 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 765 | NA | 0 | AT | 0 | Reduction because NTC over thermal limit on border | FR | 2600 | probleme coordination avec TERNA
20231010 | October | 1730 | 7861 |  |  | 7150 |  |  |  |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 711 | NA | 0 | AT | 0 | Reduction because NTC over thermal limit on border | FR | 2600 | probleme coordination avec TERNA
20231010 | October | 1830 | 7822 |  |  | 7332 |  |  |  |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 490 | NA | 0 | AT | 0 | Reduction because NTC over thermal limit on border | FR | 2600 | probleme coordination avec TERNA
20231010 | October | 1930 | 7822 |  |  | 7611 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 211 | NA | 0 | CH | 7336 | Expected overloading on the following CNEC: CNE: 380kV Gorlago - Robbia , C: N-1 SOAZZA-BULCIAGO
20231010 | October | 2030 | 7822 |  |  | 7720 |  |  |  |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 102 | NA | 0 | AT | 0 | Reduction because NTC over thermal limit on border | FR | 2600 | probleme coordination avec TERNA
20231010 | October | 2130 | 7910 |  |  | 7868 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 42 | NA | 0 | CH | 7596 | Expected overloading on the following CNEC: CNE: 380kV Gorlago - Robbia , C: N-1 SOAZZA-BULCIAGO
20231010 | October | 2230 | 7865 |  |  | 7841 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 24 | NA | 0 | CH | 7566 | Expected overloading on the following CNEC: CNE: 380kV Gorlago - Robbia , C: N-1 SOAZZA-BULCIAGO
20231010 | October | 2330 | 7070 |  |  | 7036 |  |  | AT-IT = 0 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 34 | NA | 0 | AT | 0 | Reduction because NTC over thermal limit on border
20231011 | October | 2330 | 6948 |  |  | 6943 |  |  | AT-IT = 0 |  | -1349 | -1349 | -1346 | Critical Branch | TTC Validation phase - bilateral reduction | 5 | NA | 0 | AT | 0 | Bilateral - Reduction becauseof disconnection of line 912 % 261
20231012 | October | 1530 | 7617 |  |  | 7319 |  |  | FR-IT = 2600 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 298 | NA | 0 | FR | 2600 | Bilateral - N-2 ALBERVILLE G.ILE / CREYS GENISSIAT 1
20231012 | October | 1630 | 7617 |  |  | 7319 |  |  | FR-IT = 2600 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 298 | NA | 0 | FR | 2600 | Bilateral - N-2 ALBERVILLE G.ILE / CREYS GENISSIAT 1
20231012 | October | 1730 | 8517 |  |  | 7861 |  |  | FR-IT = 2600 |  | 0 | 0 | 0 | Critical Branch | Validation phase | 656 | NA | 0 | FR | 2600 | Bilateral - N-2 ALBERVILLE G.ILE / CREYS GENISSIAT 1
20231012 | October | 1830 | 8174 |  |  | 7846 |  |  | FR-IT = 2600 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 328 | NA | 0 | FR | 2600 | Bilateral - N-2 ALBERVILLE G.ILE / CREYS GENISSIAT 1
20231012 | October | 1930 | 8174 |  |  | 7846 |  |  | FR-IT = 2600 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 328 | NA | 0 | FR | 2600 | Bilateral - N-2 ALBERVILLE G.ILE / CREYS GENISSIAT 1
20231012 | October | 2030 | 8174 |  |  | 7846 |  |  | FR-IT = 2600 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 328 | NA | 0 | FR | 2600 | Bilateral - N-2 ALBERVILLE G.ILE / CREYS GENISSIAT 1
20231012 | October | 2130 | 9110 |  |  | 7956 |  |  | FR-IT = 2600 |  | 0 | 0 | 0 | Critical Branch | Validation phase | 1154 | NA | 0 | FR | 2600 | Bilateral - N-2 ALBERVILLE G.ILE / CREYS GENISSIAT 1
20231012 | October | 2230 | 8103 |  |  | 7819 |  |  | FR-IT = 2600 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 284 | NA | 0 | FR | 2600 | Bilateral - N-2 ALBERVILLE G.ILE / CREYS GENISSIAT 1
20231012 | October | 2330 | 7308 |  |  | 7176 |  |  | FR-IT = 2600 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 132 | NA | 0 | FR | 2600 | Bilateral - N-2 ALBERVILLE G.ILE / CREYS GENISSIAT 1
20231013 | October | 1230 | 8092 |  |  | 8091 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Critical Branch | 1 | NA | 0
20231013 | October | 1330 | 8092 |  |  | 8091 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Critical Branch | 1 | NA | 0
20231013 | October | 1530 | 9583 |  |  | 8062 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 1521 | NA | 0 | CH | 7872 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231013 | October | 1630 | 9583 |  |  | 8680 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 903 | NA | 0 | CH | 8490 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231013 | October | 1730 | 10483 |  |  | 7747 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 2736 | NA | 0 | CH | 7557 | Expected overloading on the following CNEC: CNE: 380kV Filisur - Sils , C: 380KV GORLAGO-ROBBIA
20231013 | October | 1830 | 9029 |  |  | 8989 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 40 | NA | 0 | CH | 8799 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 Pradella-Robbia + Filisur-Robbia
20231013 | October | 1930 | 9029 |  |  | 8598 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 431 | NA | 0 | CH | 8408 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231013 | October | 2030 | 9029 |  |  | 8997 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 32 | NA | 0 | CH | 8807 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 Pradella-Robbia + Filisur-Robbia
20231013 | October | 2130 | 8840 |  |  | 8623 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 217 | NA | 0 | CH | 8432 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 Pradella-Robbia + Filisur-Robbia
20231013 | October | 2230 | 8840 |  |  | 8494 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 346 | NA | 0 | CH | 8303 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 Pradella-Robbia + Filisur-Robbia
20231013 | October | 2330 | 8045 |  |  | 8044 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Critical Branch | 1 | NA | 0
20231014 | October | 1530 | 8212 |  |  | 7998 |  |  | FR-IT = 2600 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 214 | NA | 0 | FR | 2600 | Bilateral - Probleme coordination Terna
20231014 | October | 1630 | 8212 |  |  | 7998 |  |  | FR-IT = 2600 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 214 | NA | 0 | FR | 2600 | Bilateral - Probleme coordination Terna
20231014 | October | 1730 | 8212 |  |  | 7998 |  |  | FR-IT = 2600 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 214 | NA | 0 | FR | 2600 | Bilateral - Probleme coordination Terna
20231014 | October | 1830 | 9149 |  |  | 8791 |  |  | FR-IT = 2600 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 358 | NA | 0 | FR | 2600 | Bilateral - Probleme coordination Terna
20231014 | October | 1930 | 9149 |  |  | 8791 |  |  | FR-IT = 2600 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 358 | NA | 0 | FR | 2600 | Bilateral - Probleme coordination Terna
20231014 | October | 2030 | 9149 |  |  | 8791 |  |  | FR-IT = 2600 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 358 | NA | 0 | FR | 2600 | Bilateral - Probleme coordination Terna
20231015 | October | 1830 | 8808 |  |  | 8578 |  |  | FR-IT = 2600 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 230 | NA | 0 | FR | 2600 | Bilateral - Probleme coordination Terna
20231015 | October | 1930 | 8808 |  |  | 8578 |  |  | FR-IT = 2600 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 230 | NA | 0 | FR | 2600 | Bilateral - Probleme coordination Terna
20231015 | October | 2030 | 8808 |  |  | 8578 |  |  | FR-IT = 2600 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 230 | NA | 0 | FR | 2600 | Bilateral - Probleme coordination Terna
20231017 | October | 1230 | 6951 |  |  | 6354 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 597 | NA | 0 | CH | 6163 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231017 | October | 2130 | 7247 |  |  | 7246 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Critical Branch | 1 | NA | 0
20231017 | October | 2230 | 7247 |  |  | 7246 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Critical Branch | 1 | NA | 0
20231018 | October | 1230 | 8095 |  |  | 6374 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 1721 | NA | 0 | CH | 6183 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 ALBERTVILLE-RONDISSONE
20231018 | October | 1330 | 8095 |  |  | 6026 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 2069 | NA | 0 | CH | 5836 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Pradella-Robbia + Filisur-Robbia
20231018 | October | 1430 | 8095 |  |  | 6197 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 1898 | NA | 0 | CH | 6007 | Expected overloading on the following CNEC: CNE: 380kV Fiorano - Robbia , C: N-2 ALBERTVILLE-RONDISSONE
20231018 | October | 1530 | 7320 |  |  | 6841 |  |  |  |  | -2950 | -2950 | -2472 | Critical Branch | Validation phase | 479 | NA | 0 | CH | 6651 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231018 | October | 1630 | 7320 |  |  | 6633 |  |  |  |  | -2950 | -2950 | -2263 | Critical Branch | Validation phase | 687 | NA | 0 | CH | 6444 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Pradella-Robbia + Filisur-Robbia
20231018 | October | 1730 | 7320 |  |  | 6645 |  |  |  |  | -2950 | -2950 | -2275 | Critical Branch | Validation phase | 675 | NA | 0 | CH | 6454 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231018 | October | 1830 | 7564 |  |  | 6293 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 1271 | NA | 0 | CH | 6102 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231018 | October | 1930 | 7564 |  |  | 6592 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 972 | NA | 0 | CH | 6402 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231018 | October | 2030 | 7564 |  |  | 7078 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 486 | NA | 0 | CH | 6888 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Pradella-Robbia + Filisur-Robbia
20231018 | October | 2130 | 7875 |  |  | 6422 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 1453 | NA | 0 | CH | 6232 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231018 | October | 2230 | 7875 |  |  | 5953 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 1922 | NA | 0 | CH | 5764 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231018 | October | 2330 | 7280 |  |  | 6281 |  |  |  |  | -3472 | -3472 | -2473 | Critical Branch | Validation phase | 999 | NA | 0 | CH | 6086 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Pradella-Robbia + Filisur-Robbia
20231019 | October | 1730 | 6345 |  |  | 6338 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 7 | NA | 0 | CH | 6148 | Expected overloading on the following CNEC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231019 | October | 1830 | 6653 |  |  | 6565 |  |  | FR-IT = 2050 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 88 | NA | 0 | FR | 1400 | Bilateral - n-2Albertville Grand ile
20231019 | October | 1930 | 6653 |  |  | 6397 |  |  | FR-IT = 1883 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 256 | NA | 0 | FR | 1400 | Bilateral - n-2Albertville Grand ile
20231019 | October | 2030 | 6653 |  |  | 6397 |  |  | FR-IT = 1883 |  | -2398 | -2398 | -2184 | Critical Branch | TTC Validation phase - bilateral reduction | 256 | NA | 0 | FR | 1400 | Bilateral - n-2Albertville Grand ile
20231019 | October | 2130 | 6588 |  |  | 5135 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | Validation phase | 1453 | NA | 0 | CH | 4945 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231019 | October | 2230 | 6588 |  |  | 5135 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | Validation phase | 1453 | NA | 0 | CH | 4945 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231022 | October | 1230 | 6061 |  |  | 5879 |  |  | FR-IT = 1400 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 182 | NA | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT
20231022 | October | 1330 | 6061 |  |  | 5879 |  |  | FR-IT = 1400 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 182 | NA | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT
20231022 | October | 1430 | 6061 |  |  | 5863 |  |  | FR-IT = 1400 |  | 0 | 0 | 0 | Critical Branch | Validation phase | 198 | NA | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT
20231022 | October | 1530 | 5978 |  |  | 5899 |  |  | FR-IT = 1400 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 79 | NA | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT
20231022 | October | 1630 | 5978 |  |  | 5899 |  |  | FR-IT = 1400 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 79 | NA | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT
20231022 | October | 1730 | 5978 |  |  | 5899 |  |  | FR-IT = 1400 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 79 | NA | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT
20231022 | October | 2130 | 7011 |  |  | 6097 |  |  | FR-IT = 1406 |  | 0 | 0 | 0 | Critical Branch | Validation phase | 914 | NA | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT
20231022 | October | 2230 | 7011 |  |  | 6165 |  |  | FR-IT = 1406 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 846 | NA | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT
20231022 | October | 2330 | 7011 |  |  | 6166 |  |  | FR-IT = 1406 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 845 | NA | 0 | FR | 1400 | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT
20231023 | October | 1230 | 6783 |  |  | 5687 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 1096 | NA | 0 | AT | 0 | Reduction because NTC over thermal limit on border | FR | 1400 | N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT
20231023 | October | 1330 | 6783 |  |  | 5170 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 1613 | NA | 0 | CH | 4980 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20231023 | October | 1430 | 6783 |  |  | 5170 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 1613 | NA | 0 | CH | 4980 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20231023 | October | 1530 | 6445 |  |  | 5615 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 830 | NA | 0 | CH | 5425 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20231023 | October | 1630 | 6445 |  |  | 5615 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 830 | NA | 0 | CH | 5425 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20231023 | October | 1730 | 6445 |  |  | 5615 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 830 | NA | 0 | CH | 5425 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20231023 | October | 1830 | 5915 |  |  | 5665 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 250 | NA | 0 | CH | 5475 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20231023 | October | 1930 | 5915 |  |  | 5665 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 250 | NA | 0 | CH | 5475 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20231023 | October | 2030 | 5915 |  |  | 5665 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 250 | NA | 0 | CH | 5475 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20231023 | October | 2130 | 7010 |  |  | 5612 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 1398 | NA | 0 | CH | 5422 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20231023 | October | 2230 | 6377 |  |  | 5612 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 765 | NA | 0 | CH | 5422 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20231023 | October | 2330 | 5782 |  |  | 5167 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 615 | NA | 0 | CH | 4974 | IT issues in internal Validation Tool. BackUp-NTC-values are applied.
20231024 | October | 1230 | 7010 |  |  | 5672 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1338 | NA | 0 | AT | 0 | Reduction because NTC over thermal limit on border | FR | 1400 | N-2 ALBERTVILLE- RONDISSONE
20231024 | October | 1330 | 7010 |  |  | 5594 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1416 | NA | 0 | AT | 0 | Reduction because NTC over thermal limit on border | FR | 1400 | N-2 ALBERTVILLE- RONDISSONE
20231024 | October | 1430 | 7010 |  |  | 5753 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1257 | NA | 0 | AT | 0 | Reduction because NTC over thermal limit on border | FR | 1400 | N-2 ALBERTVILLE- RONDISSONE
20231024 | October | 1530 | 6880 |  |  | 5596 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 1284 | NA | 0 | AT | 0 | Reduction because NTC over thermal limit on border | FR | 1400 | N-2 ALBERTVILLE- RONDISSONE
20231024 | October | 1630 | 6880 |  |  | 5596 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 1284 | NA | 0 | AT | 0 | Reduction because NTC over thermal limit on border | FR | 1400 | N-2 ALBERTVILLE- RONDISSONE
20231024 | October | 1730 | 6880 |  |  | 5596 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 1284 | NA | 0 | AT | 0 | Reduction because NTC over thermal limit on border | FR | 1400 | N-2 ALBERTVILLE- RONDISSONE
20231024 | October | 1830 | 6638 |  |  | 5405 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 1233 | NA | 0 | AT | 0 | Reduction because NTC over thermal limit on border | FR | 1400 | N-2 ALBERTVILLE- RONDISSONE
20231024 | October | 1930 | 6638 |  |  | 5373 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 1265 | NA | 0 | AT | 0 | Reduction because NTC over thermal limit on border | FR | 1400 | N-2 ALBERTVILLE- RONDISSONE
20231024 | October | 2030 | 6638 |  |  | 5398 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 1240 | NA | 0 | AT | 0 | Reduction because NTC over thermal limit on border | FR | 1400 | N-2 ALBERTVILLE- RONDISSONE
20231024 | October | 2130 | 7014 |  |  | 5680 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 1334 | NA | 0 | AT | 0 | Reduction because NTC over thermal limit on border | FR | 1400 | N-2 ALBERTVILLE- RONDISSONE
20231024 | October | 2230 | 7014 |  |  | 5625 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 1389 | NA | 0 | AT | 0 | Reduction because NTC over thermal limit on border | FR | 1400 | N-2 ALBERTVILLE- RONDISSONE
20231024 | October | 2330 | 6419 |  |  | 5235 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 1184 | NA | 0 | AT | 0 | Reduction because NTC over thermal limit on border | FR | 1400 | N-2 ALBERTVILLE- RONDISSONE
20231025 | October | 1230 | 6200 |  |  | 6013 |  |  | FR-IT = 1400 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 187 | NA | 0 | FR | 1400 | Bilateral - N-2 Albertville Rondissone / Albertville-Grande Ile
20231025 | October | 1330 | 6200 |  |  | 6013 |  |  | FR-IT = 1400 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 187 | NA | 0 | FR | 1400 | Bilateral - N-2 Albertville Rondissone / Albertville-Grande Ile
20231025 | October | 1430 | 6200 |  |  | 6013 |  |  | FR-IT = 1400 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 187 | NA | 0 | FR | 1400 | Bilateral - N-2 Albertville Rondissone / Albertville-Grande Ile
20231025 | October | 1530 | 6479 |  |  | 6321 |  |  | FR-IT = 1400 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 158 | NA | 0 | FR | 1400 | Bilateral - N-2 Albertville Rondissone / Albertville-Grande Ile
20231025 | October | 1630 | 6479 |  |  | 6202 |  |  | FR-IT = 1400 |  | 0 | 0 | 0 | Critical Branch | Validation phase | 277 | NA | 0 | FR | 1400 | Bilateral - N-2 Albertville Rondissone / Albertville-Grande Ile
20231025 | October | 1730 | 6719 |  |  | 6568 |  |  | FR-IT = 1400 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 151 | NA | 0 | FR | 1400 | Bilateral - N-2 Albertville Rondissone / Albertville-Grande Ile
20231025 | October | 1830 | 7058 |  |  | 6492 |  |  | FR-IT = 1400 |  | 0 | 0 | 0 | Critical Branch | Validation phase | 566 | NA | 0 | FR | 1400 | Bilateral - N-2 Albertville Rondissone / Albertville-Grande Ile
20231025 | October | 1930 | 7058 |  |  | 6424 |  |  | FR-IT = 1400 |  | 0 | 0 | 0 | Critical Branch | Validation phase | 634 | NA | 0 | FR | 1400 | Bilateral - N-2 Albertville Rondissone / Albertville-Grande Ile
20231025 | October | 2030 | 7058 |  |  | 6850 |  |  | FR-IT = 1400 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 208 | NA | 0 | FR | 1400 | Bilateral - N-2 Albertville Rondissone / Albertville-Grande Ile
20231025 | October | 2130 | 6889 |  |  | 6285 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 604 | NA | 0 | CH | 6095 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231025 | October | 2230 | 6889 |  |  | 6285 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 604 | NA | 0 | CH | 6095 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231025 | October | 2330 | 6279 |  |  | 5959 |  |  | FR-IT = 1400 |  | 0 | 0 | 0 | Critical Branch | Validation phase | 320 | NA | 0 | FR | 1400 | Bilateral - N-2 Albertville Rondissone / Albertville-Grande Ile
20231026 | October | 1230 | 6856 |  |  | 6406 |  |  | FR-IT = 1400 |  | 0 | 0 | 0 | Critical Branch | Validation phase | 450 | NA | 0 | FR | 1400 | Bilateral - N-2 Albertville-Rondissonne / Albertville - Grande-Ile
20231026 | October | 1330 | 6856 |  |  | 6494 |  |  | FR-IT = 1400 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 362 | NA | 0 | FR | 1400 | Bilateral - N-2 Albertville-Rondissonne / Albertville - Grande-Ile
20231026 | October | 1430 | 6856 |  |  | 6435 |  |  | FR-IT = 1400 |  | 0 | 0 | 0 | Critical Branch | Validation phase | 421 | NA | 0 | FR | 1400 | Bilateral - N-2 Albertville-Rondissonne / Albertville - Grande-Ile
20231026 | October | 1530 | 6697 |  |  | 6379 |  |  | FR-IT = 1400 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 318 | NA | 0 | FR | 1400 | Bilateral - N-2 Albertville-Rondissonne / Albertville - Grande-Ile
20231026 | October | 1630 | 6697 |  |  | 6379 |  |  | FR-IT = 1400 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 318 | NA | 0 | FR | 1400 | Bilateral - N-2 Albertville-Rondissonne / Albertville - Grande-Ile
20231026 | October | 1730 | 6697 |  |  | 5887 |  |  | FR-IT = 1400 |  | 0 | 0 | 0 | Critical Branch | Validation phase | 810 | NA | 0 | FR | 1400 | Bilateral - N-2 Albertville-Rondissonne / Albertville - Grande-Ile
20231026 | October | 2130 | 6650 |  |  | 6346 |  |  | FR-IT = 1400 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 304 | NA | 0 | FR | 1400 | Bilateral - N-2 Albertville-Rondissonne / Albertville - Grande-Ile
20231026 | October | 2230 | 6442 |  |  | 6195 |  |  | FR-IT = 1400 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 247 | NA | 0 | FR | 1400 | Bilateral - N-2 Albertville-Rondissonne / Albertville - Grande-Ile
20231026 | October | 2330 | 5832 |  |  | 5739 |  |  | FR-IT = 1400 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 93 | NA | 0 | FR | 1400 | Bilateral - N-2 Albertville-Rondissonne / Albertville - Grande-Ile
20231027 | October | 1230 | 7582 |  |  | 5669 |  |  | FR-IT = 1400 |  | 0 | 0 | 0 | Critical Branch | Validation phase | 1913 | NA | 0 | FR | 1400 | Bilateral - N-2 Albertville-Rondissonne / Albertville-G.Ile
20231027 | October | 1330 | 7582 |  |  | 5842 |  |  | FR-IT = 1400 |  | 0 | 0 | 0 | Critical Branch | Validation phase | 1740 | NA | 0 | FR | 1400 | Bilateral - N-2 Albertville-Rondissonne / Albertville - G.Ile
20231027 | October | 1430 | 7582 |  |  | 6084 |  |  | FR-IT = 1400 |  | 0 | 0 | 0 | Critical Branch | Validation phase | 1498 | NA | 0 | FR | 1400 | Bilateral - N-2 Albertville-Rondissonne / Albertville - G.Ile
20231027 | October | 1530 | 6561 |  |  | 6292 |  |  | FR-IT = 1400 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 269 | NA | 0 | FR | 1400 | Bilateral - N-2 Albertville-Rondissonne / Albertville - G.Ile
20231027 | October | 1630 | 6561 |  |  | 6292 |  |  | FR-IT = 1400 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 269 | NA | 0 | FR | 1400 | Bilateral - N-2 Albertville-Rondissonne / Albertville - G.Ile
20231027 | October | 1730 | 7861 |  |  | 7334 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 527 | NA | 0 | CH | 7144 | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE
20231027 | October | 1830 | 8148 |  |  | 6627 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 1521 | NA | 0 | CH | 6437 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231027 | October | 1930 | 8148 |  |  | 6714 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 1434 | NA | 0 | CH | 6524 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231027 | October | 2030 | 8148 |  |  | 7385 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 763 | NA | 0 | CH | 7195 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231029 | October | 1230 | 7254 |  |  | 7240 |  |  | AT-IT = 208 |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 14 | NA | 0 | AT | 208 | Bilateral - Reduction because of outageof line 912
20231029 | October | 1530 | 6813 |  |  | 6812 |  |  | AT-IT = 207 |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 1 | NA | 0 | AT | 207 | Bilateral - Reduction because of outageof line 912
20231030 | October | 1230 | 8599 |  |  | 7420 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 1179 | NA | 0 | CH | 7231 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231030 | October | 1330 | 8599 |  |  | 7782 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 817 | NA | 0 | CH | 7591 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231030 | October | 1430 | 8599 |  |  | 7033 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 1566 | NA | 0 | CH | 6843 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231030 | October | 1530 | 8731 |  |  | 6952 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 1779 | NA | 0 | CH | 6762 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231030 | October | 1630 | 8731 |  |  | 6961 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 1770 | NA | 0 | CH | 6771 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231030 | October | 1730 | 8731 |  |  | 6567 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 2164 | NA | 0 | CH | 6350 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231030 | October | 1830 | 8312 |  |  | 7459 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 853 | NA | 0 | CH | 7268 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231030 | October | 1930 | 8312 |  |  | 7304 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 1008 | NA | 0 | CH | 7115 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231030 | October | 2030 | 8312 |  |  | 7594 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 718 | NA | 0 | CH | 7404 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231030 | October | 2130 | 8630 |  |  | 7071 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 1559 | NA | 0 | CH | 6881 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231030 | October | 2230 | 8630 |  |  | 7173 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 1457 | NA | 0 | CH | 6979 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231030 | October | 2330 | 8020 |  |  | 7813 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 207 | NA | 0 | CH | 7543 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231031 | October | 1230 | 7839 |  |  | 7210 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Scheduled TTC | 629 | NA | 0 | Fictive flag
20231031 | October | 1330 | 7839 |  |  | 7210 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Scheduled TTC | 629 | NA | 0 | Fictive flag
20231031 | October | 1430 | 7839 |  |  | 7210 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Scheduled TTC | 629 | NA | 0 | Fictive flag
20231031 | October | 1530 | 7978 |  |  | 7675 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Scheduled TTC | 303 | NA | 0 | Fictive flag
20231031 | October | 1630 | 7978 |  |  | 7675 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Scheduled TTC | 303 | NA | 0 | Fictive flag
20231031 | October | 1730 | 7978 |  |  | 7675 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Scheduled TTC | 303 | NA | 0 | Fictive flag
20231031 | October | 1830 | 7545 |  |  | 7485 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Scheduled TTC | 60 | NA | 0 | Fictive flag
20231031 | October | 1930 | 7545 |  |  | 7485 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Scheduled TTC | 60 | NA | 0 | Fictive flag
20231031 | October | 2030 | 7545 |  |  | 7485 |  |  | AT-IT = 225 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 60 | NA | 0 | AT | -100000 | Bilateral - Because of high redispatch the leftover intraday capacity was set to 0
20231101 | November | 1330 | 7280 |  |  | 7279 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Critical Branch | 1 | NA | 0
20231102 | November | 1230 | 6950 |  |  | 6160 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Scheduled TTC | 790 | NA | 0 | Fictive flag
20231102 | November | 1330 | 6950 |  |  | 6160 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Scheduled TTC | 790 | NA | 0 | Fictive flag
20231102 | November | 1430 | 6950 |  |  | 6160 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Scheduled TTC | 790 | NA | 0 | Fictive flag
20231102 | November | 1530 | 7489 |  |  | 6752 |  |  | FR-IT = 2797 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 737 | NA | 0 | FR | 2532 | Bilateral - N-2 ALBERTVILLE - RONDISSONE
20231102 | November | 1630 | 7489 |  |  | 6752 |  |  | FR-IT = 2797 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 737 | NA | 0 | FR | 2532 | Bilateral - N-2 ALBERTVILLE - RONDISSONE
20231102 | November | 1730 | 7489 |  |  | 6752 |  |  | FR-IT = 2797 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 737 | NA | 0 | FR | 2532 | Bilateral - N-2 ALBERTVILLE - RONDISSONE
20231102 | November | 1830 | 7180 |  |  | 6594 |  |  | FR-IT = 2726 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 586 | NA | 0 | FR | 2532 | Bilateral - N-2 ALBERTVILLE - RONDISSONE
20231102 | November | 1930 | 7180 |  |  | 6594 |  |  | FR-IT = 2726 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 586 | NA | 0 | FR | 2532 | Bilateral - N-2 ALBERTVILLE - RONDISSONE
20231102 | November | 2030 | 7180 |  |  | 6594 |  |  | FR-IT = 2726 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 586 | NA | 0 | FR | 2532 | Bilateral - N-2 ALBERTVILLE - RONDISSONE
20231102 | November | 2130 | 7312 |  |  | 6744 |  |  | FR-IT = 2793 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 568 | NA | 0 | FR | 2532 | Bilateral - N-2 ALBERTVILLE - RONDISSONE
20231102 | November | 2230 | 7312 |  |  | 6744 |  |  | FR-IT = 2793 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 568 | NA | 0 | FR | 2532 | Bilateral - N-2 ALBERTVILLE - RONDISSONE
20231102 | November | 2330 | 6717 |  |  | 6055 |  |  | FR-IT = 2532 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 662 | NA | 0 | FR | 2532 | Bilateral - N-2 ALBERTVILLE - RONDISSONE
20231103 | November | 1530 | 8078 |  |  | 8031 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 47 | NA | 0 | CH | 7841 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231104 | November | 1530 | 9688 |  |  | 9687 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Critical Branch | 1 | NA | 0
20231104 | November | 1630 | 9688 |  |  | 9687 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Critical Branch | 1 | NA | 0
20231104 | November | 1730 | 11088 |  |  | 9642 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 1446 | NA | 0 | CH | 9452 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231106 | November | 1730 | 9091 |  |  | 8693 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 398 | NA | 0 | CH | 8503 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231106 | November | 1830 | 8750 |  |  | 8025 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 725 | NA | 0 | CH | 7835 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231106 | November | 1930 | 8750 |  |  | 8716 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 34 | NA | 0 | CH | 8526 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231106 | November | 2030 | 8750 |  |  | 8515 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 235 | NA | 0 | CH | 8325 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231106 | November | 2130 | 8605 |  |  | 8450 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 155 | NA | 0 | CH | 8260 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231108 | November | 1830 | 9350 |  |  | 9039 |  |  |  |  | -2564 | -2564 | -2253 | Critical Branch | Validation phase | 311 | NA | 0 | CH | 8849 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231108 | November | 1930 | 8800 |  |  | 8690 |  |  |  |  | -2014 | -2014 | -1944 | Critical Branch | Validation phase | 110 | NA | 0 | CH | 8500 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231108 | November | 2030 | 9350 |  |  | 8802 |  |  |  |  | -2564 | -2564 | -2027 | Critical Branch | Validation phase | 548 | NA | 0 | CH | 8612 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231109 | November | 1230 | 9440 |  |  | 9251 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 189 | NA | 0 | CH | 9061 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231109 | November | 1330 | 9440 |  |  | 9046 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 394 | NA | 0 | CH | 8855 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231109 | November | 1430 | 9440 |  |  | 9069 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 371 | NA | 0 | CH | 8879 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231109 | November | 1530 | 9271 |  |  | 9270 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Critical Branch | 1 | NA | 0
20231109 | November | 1630 | 9271 |  |  | 9223 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 48 | NA | 0 | CH | 9032 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231109 | November | 1730 | 9571 |  |  | 9034 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 537 | NA | 0 | CH | 8844 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231109 | November | 1830 | 9352 |  |  | 8946 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 406 | NA | 0 | CH | 8755 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231109 | November | 1930 | 9352 |  |  | 9118 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 234 | NA | 0 | CH | 8928 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231109 | November | 2030 | 9352 |  |  | 8905 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 447 | NA | 0 | CH | 8715 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231109 | November | 2130 | 9171 |  |  | 8535 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 636 | NA | 0 | CH | 8345 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 Pradella-Robbia + Filisur-Robbia
20231109 | November | 2230 | 9171 |  |  | 8387 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 784 | NA | 0 | CH | 8192 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231110 | November | 1530 | 9224 |  |  | 9223 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Critical Branch | 1 | NA | 0
20231110 | November | 1630 | 9224 |  |  | 9223 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Critical Branch | 1 | NA | 0
20231111 | November | 1530 | 8246 |  |  | 8233 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Smoothing ramp | 13 | NA | 0 | Smoothing
20231111 | November | 1730 | 8546 |  |  | 8329 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Smoothing ramp | 217 | NA | 0 | Smoothing
20231111 | November | 1830 | 8640 |  |  | 8393 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 247 | NA | 0 | CH | 8203 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231111 | November | 2030 | 8640 |  |  | 8606 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 34 | NA | 0 | CH | 8416 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231113 | November | 1230 | 8557 |  |  | 8241 |  |  | FR-IT = 2385 |  | -2733 | -2733 | -2111 | Critical Branch | TTC Validation phase - bilateral reduction | 316 | NA | 0 | FR | 2385 | Bilateral - RDCR CORNIER GENISSIAT
20231113 | November | 1330 | 8557 |  |  | 8241 |  |  | FR-IT = 2385 |  | -2733 | -2733 | -2111 | Critical Branch | TTC Validation phase - bilateral reduction | 316 | NA | 0 | FR | 2385 | Bilateral - RDCR CORNIER GENISSIAT
20231113 | November | 1430 | 8557 |  |  | 8241 |  |  | FR-IT = 2385 |  | -2733 | -2733 | -2111 | Critical Branch | TTC Validation phase - bilateral reduction | 316 | NA | 0 | FR | 2385 | Bilateral - RDCR CORNIER GENISSIAT
20231113 | November | 1830 | 8617 |  |  | 8108 |  |  | FR-IT = 2385 |  | -1297 | -1297 | -730 | Critical Branch | Validation phase | 509 | NA | 0 | FR | 2385 | Bilateral - RDCR CORNIER GENISSIAT
20231113 | November | 1930 | 8617 |  |  | 8391 |  |  | FR-IT = 2385 |  | -1297 | -1297 | -929 | Critical Branch | TTC Validation phase - bilateral reduction | 226 | NA | 0 | FR | 2385 | Bilateral - RDCR CORNIER GENISSIAT
20231113 | November | 2030 | 8617 |  |  | 8291 |  |  | FR-IT = 2385 |  | -1297 | -1297 | -859 | Critical Branch | Validation phase | 326 | NA | 0 | FR | 2385 | Bilateral - RDCR CORNIER GENISSIAT
20231113 | November | 2130 | 8837 |  |  | 8722 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 115 | NA | 0 | CH | 8532 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231113 | November | 2230 | 8837 |  |  | 8655 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 182 | NA | 0 | CH | 8460 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231113 | November | 2330 | 8563 |  |  | 8361 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 202 | NA | 0 | CH | 8091 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231114 | November | 1530 | 8734 |  |  | 8733 |  |  |  |  | -1234 | -1234 | -1233 | Critical Branch | Critical Branch | 1 | NA | 0
20231114 | November | 1630 | 8734 |  |  | 8733 |  |  |  |  | -1234 | -1234 | -1233 | Critical Branch | Critical Branch | 1 | NA | 0
20231114 | November | 2130 | 8438 |  |  | 8366 |  |  |  |  | -1729 | -1729 | -1666 | Critical Branch | Validation phase | 72 | NA | 0 | CH | 8176 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231114 | November | 2230 | 8438 |  |  | 8421 |  |  |  |  | -1729 | -1729 | -1715 | Critical Branch | Validation phase | 17 | NA | 0 | CH | 8198 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231115 | November | 1230 | 8624 |  |  | 8621 |  |  | FR-IT = 2534 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 3 | NA | 0 | FR | 2400 | Bilateral - N-2 ALBERTVILLE G.ILE
20231115 | November | 1330 | 8624 |  |  | 8621 |  |  | FR-IT = 2534 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 3 | NA | 0 | FR | 2400 | Bilateral - N-2 ALBERTVILLE G.ILE
20231115 | November | 1430 | 8624 |  |  | 8621 |  |  | FR-IT = 2534 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 3 | NA | 0 | FR | 2400 | Bilateral - N-2 ALBERTVILLE G.ILE
20231115 | November | 1530 | 8560 |  |  | 8534 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 26 | NA | 0 | CH | 8344 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231115 | November | 1730 | 9760 |  |  | 9235 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 525 | NA | 0 | CH | 9045 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231116 | November | 1230 | 9396 |  |  | 9386 |  |  | AT-IT = 236 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 10 | NA | 0 | AT | -100000 | Bilateral - Because of high redispatch the leftover intraday capacity was set to 0
20231116 | November | 1330 | 9396 |  |  | 9386 |  |  | AT-IT = 236 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 10 | NA | 0 | AT | -100000 | Bilateral - Because of high redispatch the leftover intraday capacity was set to 0
20231116 | November | 1430 | 9396 |  |  | 9180 |  |  | AT-IT = 30 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 216 | NA | 0 | AT | -100000 | Bilateral - Because of high redispatch the leftover intraday capacity was set to 0
20231116 | November | 1530 | 9158 |  |  | 9154 |  |  | AT-IT = 238 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 4 | NA | 0 | AT | -100000 | Bilateral - Because of high redispatch the leftover intraday capacity was set to 0
20231116 | November | 1630 | 9158 |  |  | 9060 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 98 | NA | 0 | CH | 8785 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE
20231116 | November | 1730 | 9458 |  |  | 9452 |  |  | AT-IT = 235 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 6 | NA | 0 | AT | -100000 | Bilateral - Because of high redispatch the leftover intraday capacity was set to 0
20231116 | November | 1830 | 9166 |  |  | 8669 |  |  | AT-IT = 228 |  | 0 | 0 | 0 | Critical Branch | Validation phase | 497 | NA | 0 | AT | 249 | Bilateral - Because of high redispatch the leftover intraday capacity was set to 0
20231116 | November | 2130 | 9350 |  |  | 9349 |  |  | AT-IT = 240 |  | 0 | 0 | 0 | Critical Branch | Critical Branch | 1 | NA | 0 | AT | 254 | Bilateral - Because of high redispatch the leftover intraday capacity was set to 0
20231118 | November | 1330 | 4495 |  |  | 4494 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | GSK Limitation | 1 | NA | 0
20231118 | November | 1530 | 8778 |  |  | 8367 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | 411 | NA | 0 | Smoothing
20231119 | November | 1530 | 8951 |  |  | 8928 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 23 | NA | 0 | CH | 8653 | Expected overloading on the following CNEC: CNE: 380kV Fiorano - Robbia , C: 380KV GORLAGO-ROBBIA
20231119 | November | 1630 | 8951 |  |  | 7882 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1069 | NA | 0 | CH | 7607 | Expected overloading on the following CNEC: CNE: 380kV Fiorano - Robbia , C: 380KV GORLAGO-ROBBIA
20231119 | November | 1830 | 9435 |  |  | 8952 |  |  |  |  | 2902 | 483 | 0 | Minimum Margin | Validation phase | 483 | NA | -2419 | FR | 8677 | Process fail during TSO validation phase
20231119 | November | 1930 | 9435 |  |  | 8952 |  |  |  |  | 2902 | 483 | 0 | Minimum Margin | Validation phase | 483 | NA | -2419 | FR | 8677 | Process fail during TSO validation phase
20231119 | November | 2030 | 9435 |  |  | 8952 |  |  |  |  | 2902 | 483 | 0 | Minimum Margin | Validation phase | 483 | NA | -2419 | FR | 8677 | Process fail during TSO validation phase
20231119 | November | 2130 | 8534 |  |  | 8375 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 159 | NA | 0 | CH | 8100 | Expected overloading on the following CNEC: CNE: 380kV Fiorano - Robbia , C: 380KV GORLAGO-ROBBIA
20231119 | November | 2230 | 8534 |  |  | 8055 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 479 | NA | 0 | CH | 7780 | Expected overloading on the following CNEC: CNE: 380kV Fiorano - Robbia , C: 380KV GORLAGO-ROBBIA
20231119 | November | 2330 | 7998 |  |  | 7997 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Critical Branch | 1 | NA | 0
20231120 | November | 1230 | 9258 |  |  | 8389 |  |  | FR-IT = 2767 |  | -5602 | -5602 | -4289 | Critical Branch | Validation phase | 869 | NA | 0 | FR | 2600 | Bilateral - N-2 Alberville-Rondissone / Cornier-Riddes-St-Triphon
20231120 | November | 1330 | 9258 |  |  | 8411 |  |  | FR-IT = 2767 |  | -5602 | -5602 | -4302 | Critical Branch | Validation phase | 847 | NA | 0 | FR | 2600 | Bilateral - N-2 Alberville-Rondissone / Cornier-Riddes-St-Triphon
20231120 | November | 1430 | 9258 |  |  | 7968 |  |  | FR-IT = 2600 |  | -5478 | -5478 | -3875 | Critical Branch | Validation phase | 1290 | NA | 0 | FR | 2600 | Bilateral - N-2 Alberville-Rondissone / Cornier-Riddes-St-Triphon
20231120 | November | 1830 | 8867 |  |  | 8218 |  |  | FR-IT = 2600 |  | -2961 | -2961 | -2071 | Critical Branch | Validation phase | 649 | NA | 0 | FR | 2600 | Bilateral - N-2 Alberville-Rondissone / Cornier-Riddes-St-Triphon
20231120 | November | 1930 | 8867 |  |  | 8297 |  |  | FR-IT = 2600 |  | -2961 | -2961 | -2125 | Critical Branch | TTC Validation phase - bilateral reduction | 570 | NA | 0 | FR | 2600 | Bilateral - N-2 Alberville-Rondissone / Cornier-Riddes-St-Triphon
20231120 | November | 2030 | 8867 |  |  | 8346 |  |  | FR-IT = 2786 |  | -3067 | -3067 | -2304 | Critical Branch | TTC Validation phase - bilateral reduction | 521 | NA | 0 | FR | 2600 | Bilateral - N-2 Alberville-Rondissone / Cornier-Riddes-St-Triphon
20231120 | November | 2130 | 9240 |  |  | 8305 |  |  | FR-IT = 2786 |  | -2664 | -2664 | -1798 | Critical Branch | Validation phase | 935 | NA | 0 | FR | 2600 | Bilateral - N-2 Alberville-Rondissone / Cornier-Riddes-St-Triphon
20231120 | November | 2230 | 9240 |  |  | 8570 |  |  | FR-IT = 2786 |  | -2664 | -2664 | -2086 | Critical Branch | TTC Validation phase - bilateral reduction | 670 | NA | 0 | FR | 2600 | Bilateral - N-2 Alberville-Rondissone / Cornier-Riddes-St-Triphon
20231120 | November | 2330 | 8966 |  |  | 8684 |  |  | FR-IT = 2798 |  | -2311 | -2311 | -2063 | Critical Branch | TTC Validation phase - bilateral reduction | 282 | NA | 0 | FR | 2600 | Bilateral - N-2 Alberville-Rondissone / Cornier-Riddes-St-Triphon
20231121 | November | 1830 | 8669 |  |  | 8668 |  |  |  |  | -3115 | -3115 | -3115 | Critical Branch | Critical Branch | 1 | NA | 0
20231121 | November | 1930 | 8669 |  |  | 8668 |  |  |  |  | -3115 | -3115 | -3115 | Critical Branch | Critical Branch | 1 | NA | 0
20231121 | November | 2030 | 8669 |  |  | 8668 |  |  |  |  | -3115 | -3115 | -3115 | Critical Branch | Critical Branch | 1 | NA | 0
20231123 | November | 1630 | 8504 |  |  | 8405 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 99 | NA | 0 | CH | 8214 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Pradella-Robbia + Filisur-Robbia
20231123 | November | 1730 | 8804 |  |  | 8018 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 786 | NA | 0 | CH | 7827 | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231124 | November | 2130 | 9350 |  |  | 8069 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Validation phase | 1281 | NA | 0 | CH | 7879 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231125 | November | 1530 | 8508 |  |  | 6970 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Smoothing ramp | 1538 | NA | 0 | Smoothing
20231125 | November | 1630 | 8508 |  |  | 7886 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Smoothing ramp | 622 | NA | 0 | Smoothing
20231126 | November | 1530 | 8175 |  |  | 7640 |  |  |  |  | 0 | 0 | 0 | Critical Branch | Smoothing ramp | 535 | NA | 0 | Smoothing
20231126 | November | 1730 | 8475 |  |  | 8474 |  |  | AT-IT = 208 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1 | NA | 0 | AT | -100000 | Bilateral - Because of high redispatch the leftover intraday capacity was set to 0
20231127 | November | 1530 | 8475 |  |  | 8171 |  |  | FR-IT = 2500 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 304 | NA | 0 | FR | 2500 | Bilateral - N-1 Creys - Genissiat
20231127 | November | 1630 | 8475 |  |  | 8171 |  |  | FR-IT = 2500 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 304 | NA | 0 | FR | 2500 | Bilateral - N-1 Creys - Genissiat
20231127 | November | 1730 | 8775 |  |  | 8411 |  |  | FR-IT = 2500 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 364 | NA | 0 | FR | 2500 | Bilateral - N-1 Creys - Genissiat
20231127 | November | 1830 | 8148 |  |  | 8010 |  |  | FR-IT = 2500 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 138 | NA | 0 | FR | 2500 | Bilateral - N-1 Creys - Genissiat
20231127 | November | 1930 | 8148 |  |  | 8010 |  |  | FR-IT = 2500 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 138 | NA | 0 | FR | 2500 | Bilateral - N-1 Creys - Genissiat
20231127 | November | 2030 | 8148 |  |  | 8010 |  |  | FR-IT = 2500 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 138 | NA | 0 | FR | 2500 | Bilateral - N-1 Creys - Genissiat
20231127 | November | 2130 | 8814 |  |  | 8441 |  |  | FR-IT = 2500 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 373 | NA | 0 | FR | 2500 | Bilateral - N-1 Creys - Genissiat
20231127 | November | 2230 | 7839 |  |  | 7802 |  |  | FR-IT = 2500 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 37 | NA | 0 | FR | 2500 | Bilateral - N-1 Creys - Genissiat
20231128 | November | 1230 | 7756 |  |  | 7692 |  |  | FR-IT = 2500 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 64 | NA | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1
20231128 | November | 1330 | 7756 |  |  | 7692 |  |  | FR-IT = 2500 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 64 | NA | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1
20231128 | November | 1430 | 7756 |  |  | 7692 |  |  | FR-IT = 2500 |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 64 | NA | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1
20231203 | December | 1830 | 8992 |  |  | 7779 |  |  |  |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1213 | NA | 0 | AT | 100 | Reduction because NTC over thermal limit on border | FR | 2500 | RDCR CREYS-GENISSIAT 1
20231203 | December | 1930 | 8992 |  |  | 7779 |  |  |  |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1213 | NA | 0 | AT | 100 | Reduction because NTC over thermal limit on border | FR | 2500 | RDCR CREYS-GENISSIAT 1
20231203 | December | 2030 | 8992 |  |  | 7902 |  |  |  |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 1090 | NA | 0 | AT | 100 | Reduction because NTC over thermal limit on border | FR | 2500 | RDCR CREYS-GENISSIAT 1
20231203 | December | 2130 | 8594 |  |  | 7645 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 949 | NA | 0 | AT | 100 | Reduction because NTC over thermal limit on border | FR | 2500 | RDCR CREYS-GENISSIAT 1
20231203 | December | 2230 | 8594 |  |  | 7593 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 1001 | NA | 0 | AT | 100 | Reduction because NTC over thermal limit on border | FR | 2500 | RDCR CREYS-GENISSIAT 1
20231203 | December | 2330 | 8594 |  |  | 7594 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 1000 | NA | 0 | AT | 100 | Reduction because NTC over thermal limit on border | FR | 2500 | RDCR CREYS-GENISSIAT 1
20231204 | December | 1530 | 8498 |  |  | 7747 |  |  | FR-IT = 2500 | IT-FR = 1495 | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 751 | NA | 0 | FR | 2500 | Bilateral - RDCR B.TOLLOT-GENISSIAT et CREYS-GENISSIAT
20231204 | December | 1630 | 8498 |  |  | 7747 |  |  | FR-IT = 2500 | IT-FR = 1495 | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 751 | NA | 0 | FR | 2500 | Bilateral - RDCR B.TOLLOT-GENISSIAT et CREYS-GENISSIAT
20231204 | December | 1730 | 8498 |  |  | 7747 |  |  | FR-IT = 2500 | IT-FR = 1495 | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 751 | NA | 0 | FR | 2500 | Bilateral - RDCR B.TOLLOT-GENISSIAT et CREYS-GENISSIAT
20231204 | December | 1830 | 8630 |  |  | 7823 |  |  | FR-IT = 2500 | IT-FR = 1495 | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 807 | NA | 0 | FR | 2500 | Bilateral - RDCR B.TOLLOT-GENISSIAT et CREYS-GENISSIAT
20231204 | December | 1930 | 8630 |  |  | 7823 |  |  | FR-IT = 2500 | IT-FR = 1495 | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 807 | NA | 0 | FR | 2500 | Bilateral - RDCR B.TOLLOT-GENISSIAT et CREYS-GENISSIAT
20231204 | December | 2030 | 8630 |  |  | 7823 |  |  | FR-IT = 2500 | IT-FR = 1495 | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 807 | NA | 0 | FR | 2500 | Bilateral - RDCR B.TOLLOT-GENISSIAT et CREYS-GENISSIAT
20231204 | December | 2130 | 8494 |  |  | 7744 |  |  | FR-IT = 2500 | IT-FR = 1495 | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 750 | NA | 0 | FR | 2500 | Bilateral - RDCR B.TOLLOT-GENISSIAT et CREYS-GENISSIAT
20231204 | December | 2230 | 8494 |  |  | 7744 |  |  | FR-IT = 2500 | IT-FR = 1495 | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 750 | NA | 0 | FR | 2500 | Bilateral - RDCR B.TOLLOT-GENISSIAT et CREYS-GENISSIAT
20231204 | December | 2330 | 7679 |  |  | 7113 |  |  | FR-IT = 2500 | IT-FR = 1660 | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 566 | NA | 0 | FR | 2500 | Bilateral - RDCR B.TOLLOT-GENISSIAT et CREYS-GENISSIAT
20231205 | December | 1830 | 8698 |  |  | 8155 |  |  | FR-IT = 2500 | IT-FR = 995 | -2555 | -2555 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 543 | NA | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-GRANDE ILE sur CREYS-GENISSIAT 2
20231205 | December | 1930 | 8698 |  |  | 8155 |  |  | FR-IT = 2500 | IT-FR = 995 | -2555 | -2555 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 543 | NA | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-GRANDE ILE sur CREYS-GENISSIAT 2
20231205 | December | 2030 | 8698 |  |  | 8155 |  |  | FR-IT = 2500 | IT-FR = 995 | -2555 | -2555 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 543 | NA | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-GRANDE ILE sur CREYS-GENISSIAT 2
20231205 | December | 2130 | 8950 |  |  | 8313 |  |  | FR-IT = 2500 | IT-FR = 995 | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 637 | NA | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-GRANDE ILE sur CREYS-GENISSIAT 2
20231205 | December | 2230 | 8950 |  |  | 8313 |  |  | FR-IT = 2500 | IT-FR = 995 | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 637 | NA | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-GRANDE ILE sur CREYS-GENISSIAT 2
20231205 | December | 2330 | 8140 |  |  | 7658 |  |  | FR-IT = 2500 | IT-FR = 1160 | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 482 | NA | 0 | FR | 2500 | Bilateral - N-2 ALBERTVILLE-GRANDE ILE sur CREYS-GENISSIAT 2
20231206 | December | 2130 | 8350 |  |  | 7565 |  |  |  |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 785 | NA | 0 | AT | 85 | Reduction because NTC over thermal limit on border | FR | 2500 | N-2 albertville-Rondissone sur Creys-Genissiat
20231206 | December | 2230 | 8350 |  |  | 7565 |  |  |  |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 785 | NA | 0 | AT | 85 | Reduction because NTC over thermal limit on border | FR | 2500 | N-2 albertville-Rondissone sur Creys-Genissiat
20231206 | December | 2330 | 7740 |  |  | 7102 |  |  |  |  | 0 | 0 | 0 | Critical Branch | TTC Validation phase - bilateral reduction | 638 | NA | 0 | AT | 100 | Reduction because NTC over thermal limit on border | FR | 2500 | N-2 albertville-Rondissone sur Creys-Genissiat
20231207 | December | 1530 | 8140 |  |  | 7443 |  |  | FR-IT = 2500 | IT-FR = 995 | -3457 | -3457 | -2832 | Critical Branch | TTC Validation phase - bilateral reduction | 697 | NA | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1
20231207 | December | 1630 | 8140 |  |  | 7443 |  |  | FR-IT = 2500 | IT-FR = 995 | -3457 | -3457 | -2832 | Critical Branch | TTC Validation phase - bilateral reduction | 697 | NA | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1
20231207 | December | 1730 | 8140 |  |  | 7443 |  |  | FR-IT = 2500 | IT-FR = 995 | -3457 | -3457 | -2832 | Critical Branch | TTC Validation phase - bilateral reduction | 697 | NA | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1
20231208 | December | 1230 | 7640 |  |  | 5663 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1977 | NA | 0 | AT | 100 | Reduction because of outage of line 912 | FR | 1900 | RDCR VENAUS - PIOSSASCO
20231208 | December | 1330 | 7640 |  |  | 5807 |  |  | AT-IT = 225 | IT-AT = 100 | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1833 | NA | 0 | CH | 5608 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20231208 | December | 1430 | 7640 |  |  | 6124 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1516 | NA | 0 | AT | 100 | Reduction because of outage of line 912 | FR | 1900 | RDCR VENAUS - PIOSSASCO
20231208 | December | 1530 | 7640 |  |  | 5344 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 2296 | NA | 0 | AT | 100 | Reduction because of outage of line 912 | FR | 1900 | RDCR VENAUS - PIOSSASCO
20231208 | December | 1630 | 8690 |  |  | 6536 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 2154 | NA | 0 | AT | 100 | Reduction because of outage of line 912 | FR | 1900 | RDCR VENAUS - PIOSSASCO
20231208 | December | 1730 | 8940 |  |  | 7122 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1818 | NA | 0 | AT | 100 | Reduction because of outage of line 912 | FR | 1900 | RDCR VENAUS - PIOSSASCO
20231208 | December | 1830 | 8940 |  |  | 7740 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1200 | NA | 0 | AT | 100 | Reduction because of outage of line 912 | FR | 1900 | RDCR VENAUS - PIOSSASCO
20231209 | December | 1230 | 9550 |  |  | 5684 |  |  | AT-IT = 203 | IT-AT = 85 | 0 | 0 | 0 | Scheduled TTC | Validation phase | 3866 | NA | 0 | AT | 85 | Reduction because of outage of line 912
20231209 | December | 1330 | 9550 |  |  | 5766 |  |  | AT-IT = 203 | IT-AT = 85 | 0 | 0 | 0 | Scheduled TTC | Validation phase | 3784 | NA | 0 | AT | 85 | Reduction because of outage of line 912
20231209 | December | 1430 | 9550 |  |  | 7615 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Smoothing ramp | 1935 | NA | 0 | Smoothing
20231209 | December | 1530 | 9550 |  |  | 7708 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1842 | NA | 0 | CH | 7518 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 ALBERTVILLE-RONDISSONE 1
20231209 | December | 1630 | 9550 |  |  | 8173 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1377 | NA | 0 | CH | 7983 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20231209 | December | 1730 | 9550 |  |  | 9144 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 406 | NA | 0 | CH | 8954 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20231209 | December | 1830 | 9550 |  |  | 9173 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 377 | NA | 0 | CH | 8983 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20231209 | December | 1930 | 9550 |  |  | 9457 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 93 | NA | 0 | CH | 9267 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20231209 | December | 2030 | 9550 |  |  | 9194 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 356 | NA | 0 | CH | 9004 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20231209 | December | 2130 | 9550 |  |  | 9029 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 521 | NA | 0 | CH | 8839 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20231209 | December | 2230 | 9550 |  |  | 8823 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 727 | NA | 0 | CH | 8633 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20231210 | December | 1530 | 8276 |  |  | 7490 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 786 | NA | 0 | FR | -10000 | ATC blocked | FR | -10000 | ATC blocked | SI | -10000 | ATC blocked
20231210 | December | 1630 | 8276 |  |  | 8232 |  |  | FR-IT = 3138 | IT-FR = 1160 | 0 | 0 | 0 | Scheduled TTC | Validation phase | 44 | NA | 0 | CH | 8002 | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE
20231210 | December | 1830 | 9076 |  |  | 8740 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 336 | NA | 0 | FR | -10000 | ATC blocked | FR | -10000 | ATC blocked | SI | -10000 | ATC blocked
20231210 | December | 1930 | 9076 |  |  | 8631 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 445 | NA | 0 | FR | -10000 | ATC blocked | FR | -10000 | ATC blocked | SI | -10000 | ATC blocked
20231210 | December | 2030 | 9076 |  |  | 8565 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 511 | NA | 0 | FR | -10000 | ATC blocked | FR | -10000 | ATC blocked | SI | -10000 | ATC blocked
20231210 | December | 2130 | 9076 |  |  | 8363 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 713 | NA | 0 | FR | -10000 | ATC blocked | FR | -10000 | ATC blocked | SI | -10000 | ATC blocked
20231210 | December | 2230 | 9076 |  |  | 8389 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 687 | NA | 0 | FR | -10000 | ATC blocked | FR | -10000 | ATC blocked | SI | -10000 | ATC blocked
20231210 | December | 2330 | 8540 |  |  | 8107 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 433 | NA | 0 | FR | -10000 | ATC blocked | FR | -10000 | ATC blocked | SI | -10000 | ATC blocked
20231211 | December | 1330 | 8814 |  |  | 8574 |  |  | AT-IT = 0 | IT-AT = 0 | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 240 | NA | 0 | AT | 0 | Reduction because NTC over thermal limit on border
20231211 | December | 1430 | 8814 |  |  | 8457 |  |  | AT-IT = 0 | IT-AT = 0 | 0 | 0 | 0 | Scheduled TTC | Validation phase | 357 | NA | 0 | AT | 0 | Reduction because NTC over thermal limit on border
20231211 | December | 1530 | 8814 |  |  | 8518 |  |  | AT-IT = 0 | IT-AT = 0 | 0 | 0 | 0 | Scheduled TTC | Validation phase | 296 | NA | 0 | AT | 0 | Reduction because NTC over thermal limit on border
20231211 | December | 1630 | 8814 |  |  | 8574 |  |  | AT-IT = 0 | IT-AT = 0 | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 240 | NA | 0 | AT | 0 | Reduction because NTC over thermal limit on border
20231211 | December | 1730 | 8814 |  |  | 8574 |  |  | AT-IT = 0 | IT-AT = 0 | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 240 | NA | 0 | AT | 0 | Reduction because NTC over thermal limit on border
20231211 | December | 1830 | 8814 |  |  | 8574 |  |  | AT-IT = 0 | IT-AT = 0 | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 240 | NA | 0 | AT | 0 | Reduction because NTC over thermal limit on border
20231211 | December | 1930 | 8814 |  |  | 8574 |  |  | AT-IT = 0 | IT-AT = 0 | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 240 | NA | 0 | AT | 0 | Reduction because NTC over thermal limit on border
20231211 | December | 2030 | 8814 |  |  | 8574 |  |  | AT-IT = 0 | IT-AT = 0 | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 240 | NA | 0 | AT | 0 | Reduction because NTC over thermal limit on border
20231211 | December | 2130 | 8814 |  |  | 8574 |  |  | AT-IT = 0 | IT-AT = 0 | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 240 | NA | 0 | AT | 0 | Reduction because NTC over thermal limit on border
20231211 | December | 2230 | 8814 |  |  | 8574 |  |  | AT-IT = 0 | IT-AT = 0 | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 240 | NA | 0 | AT | 0 | Reduction because NTC over thermal limit on border
20231211 | December | 2330 | 8540 |  |  | 8315 |  |  | AT-IT = 0 | IT-AT = 0 | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | 225 | NA | 0 | AT | 0 | Reduction because NTC over thermal limit on border
20231215 | December | 1230 | 9112 |  |  | 9072 |  |  | AT-IT = 216 | IT-AT = 100 | -5945 | -5945 | -5919 | Critical Branch | TTC Validation phase - bilateral reduction | 40 | NA | 0 | AT | 100 | Because of high redispatch the leftover intraday capacity was set to 0
20231215 | December | 1330 | 9112 |  |  | 9072 |  |  | AT-IT = 216 | IT-AT = 100 | -5945 | -5945 | -5919 | Critical Branch | TTC Validation phase - bilateral reduction | 40 | NA | 0 | AT | 100 | Because of high redispatch the leftover intraday capacity was set to 0
20231215 | December | 1430 | 9112 |  |  | 9072 |  |  | AT-IT = 216 | IT-AT = 100 | -5945 | -5945 | -5919 | Critical Branch | TTC Validation phase - bilateral reduction | 40 | NA | 0 | AT | 100 | Because of high redispatch the leftover intraday capacity was set to 0
20231215 | December | 1530 | 9841 |  |  | 9823 |  |  | AT-IT = 259 | IT-AT = 100 | -5909 | -5909 | -5897 | Critical Branch | TTC Validation phase - bilateral reduction | 18 | NA | 0 | AT | 100 | Because of high redispatch the leftover intraday capacity was set to 0
20231215 | December | 1630 | 9841 |  |  | 9823 |  |  | AT-IT = 259 | IT-AT = 100 | -5909 | -5909 | -5897 | Critical Branch | TTC Validation phase - bilateral reduction | 18 | NA | 0 | AT | 100 | Because of high redispatch the leftover intraday capacity was set to 0
20231215 | December | 1730 | 9841 |  |  | 9823 |  |  | AT-IT = 259 | IT-AT = 100 | -5909 | -5909 | -5897 | Critical Branch | TTC Validation phase - bilateral reduction | 18 | NA | 0 | AT | 100 | Because of high redispatch the leftover intraday capacity was set to 0
20231217 | December | 1530 | 7892 |  |  | 7061 |  |  |  |  | -5199 | -5199 | -4180 | Critical Branch | Smoothing ramp | 831 | NA | 0 | Smoothing
20231217 | December | 1730 | 9055 |  |  | 9022 |  |  |  |  | -6362 | -6362 | -6288 | ID schedules | Smoothing ramp | 33 | NA | 0 | Smoothing
20231217 | December | 1830 | 9326 |  |  | 9299 |  |  |  |  | -8792 | -8792 | -8768 | ID schedules | Validation phase | 27 | NA | 0 | CH | 7656 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20231217 | December | 2130 | 10042 |  |  | 10040 |  |  |  |  | 0 | 0 | 0 | ID schedules | Validation phase | 2 | NA | 0 | CH | 7864 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA
20231217 | December | 2230 | 9735 |  |  | 9717 |  |  |  |  | 0 | 0 | 0 | ID schedules | Smoothing ramp | 18 | NA | 0 | Smoothing
20231219 | December | 1230 | 10377 |  |  | 10339 |  |  | AT-IT = 477 | IT-AT = 185 | 433 | 238 | 207 | Minimum Margin | TTC Validation phase - bilateral reduction | 38 | NA | 12 | AT | 185 | Because of high redispatch the leftover intraday capacity was set to 0
20231219 | December | 1330 | 10377 |  |  | 10339 |  |  | AT-IT = 477 | IT-AT = 185 | 433 | 238 | 207 | Minimum Margin | TTC Validation phase - bilateral reduction | 38 | NA | 12 | AT | 185 | Because of high redispatch the leftover intraday capacity was set to 0
20231219 | December | 1430 | 10377 |  |  | 10339 |  |  | AT-IT = 477 | IT-AT = 185 | 433 | 238 | 207 | Minimum Margin | TTC Validation phase - bilateral reduction | 38 | NA | 12 | AT | 185 | Because of high redispatch the leftover intraday capacity was set to 0
20231219 | December | 1530 | 9934 |  |  | 9913 |  |  | AT-IT = 471 | IT-AT = 185 | -1837 | -1837 | -1817 | Critical Branch | TTC Validation phase - bilateral reduction | 21 | NA | 0 | AT | 185 | Because of high redispatch the leftover intraday capacity was set to 0
20231219 | December | 1630 | 9934 |  |  | 9931 |  |  | AT-IT = 489 | IT-AT = 185 | -1837 | -1837 | -1833 | Critical Branch | TTC Validation phase - bilateral reduction | 3 | NA | 0 | AT | 185 | Because of high redispatch the leftover intraday capacity was set to 0
20231219 | December | 1730 | 9934 |  |  | 9931 |  |  | AT-IT = 489 | IT-AT = 185 | -1837 | -1837 | -1833 | Critical Branch | TTC Validation phase - bilateral reduction | 3 | NA | 0 | AT | 185 | Because of high redispatch the leftover intraday capacity was set to 0
20231220 | December | 1230 | 9864 |  |  | 9362 |  |  | AT-IT = 269 | IT-AT = 100 | -2503 | -2503 | -2010 | Critical Branch | Validation phase | 502 | NA | 0 | AT | 100 | Reduction because NTC over thermal limit on border
20231220 | December | 1330 | 9864 |  |  | 9573 |  |  | AT-IT = 278 | IT-AT = 100 | -2503 | -2503 | -2219 | Critical Branch | Validation phase | 291 | NA | 0 | AT | 100 | Reduction because NTC over thermal limit on border
20231220 | December | 1430 | 9864 |  |  | 9456 |  |  | AT-IT = 278 | IT-AT = 100 | -2503 | -2503 | -2103 | Critical Branch | Validation phase | 408 | NA | 0 | AT | 100 | Reduction because NTC over thermal limit on border
20231220 | December | 1530 | 9731 |  |  | 9360 |  |  | AT-IT = 263 | IT-AT = 100 | -1819 | -1819 | -1460 | Critical Branch | Validation phase | 371 | NA | 0 | AT | 100 | Reduction because NTC over thermal limit on border
20231220 | December | 1630 | 9731 |  |  | 9523 |  |  | AT-IT = 274 | IT-AT = 100 | -1819 | -1819 | -1624 | Critical Branch | TTC Validation phase - bilateral reduction | 208 | NA | 0 | AT | 100 | Reduction because NTC over thermal limit on border
20231220 | December | 2030 | 9735 |  |  | 9600 |  |  | AT-IT = 475 | IT-AT = 185 | -9766 | -9766 | -9632 | Critical Branch | Validation phase | 135 | NA | 0 | CH | 9342 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231222 | December | 1230 | 9219 |  |  | 8983 |  |  | AT-IT = 228 | IT-AT = 185 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | 236 | NA | 0 | AT | 185 | Reduction because NTC over thermal limit on border
20231228 | December | 1230 | 10850 |  |  | 9848 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1002 | NA | 0 | CH | 9658 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231228 | December | 1330 | 10850 |  |  | 10152 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 698 | NA | 0 | CH | 9962 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231228 | December | 1430 | 10850 |  |  | 10633 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 217 | NA | 0 | CH | 10443 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231228 | December | 1530 | 10850 |  |  | 10825 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 25 | NA | 0 | CH | 10635 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano
20231228 | December | 1630 | 10850 |  |  | 10784 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 66 | NA | 0 | CH | 10594 | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia
20231228 | December | 1730 | 10850 |  |  | 9944 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 906 | NA | 0 | CH | 9754 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20231228 | December | 1830 | 10850 |  |  | 9736 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1114 | NA | 0 | CH | 9546 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20231228 | December | 1930 | 10850 |  |  | 9534 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1316 | NA | 0 | CH | 9344 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20231228 | December | 2030 | 10850 |  |  | 8857 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1993 | NA | 0 | CH | 8392 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20231228 | December | 2130 | 10850 |  |  | 8900 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1950 | NA | 0 | CH | 8710 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20231228 | December | 2230 | 10850 |  |  | 8857 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1993 | NA | 0 | CH | 7983 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20231228 | December | 2330 | 10040 |  |  | 8220 |  |  |  |  | 0 | 0 | 0 | Scheduled TTC | Validation phase | 1820 | NA | 0 | CH | 7688 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA
20231229 | December | 2230 | 8040 |  |  | 7943 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | Validation phase | 97 | NA | 0 | CH | 7753 | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV SILS-SOAZZA
20231231 | December | 2130 | 6072 |  |  | 6048 |  |  |  |  | 0 | 0 | 0 | GSK Limitation | Smoothing ramp | 24 | NA | 0 | Smoothing
20231129 | November | 1230 |  | 7130 | 700 |  | 700 | 6522 | FR-IT = 2807 | IT-FR = 1495 | -9085 | -9085 | -9085 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 608 | 0 | FR | 2500 | Bilateral - CREYS GENISSIAT 1
20231129 | November | 1330 |  | 7130 | 700 |  | 700 | 6532 | FR-IT = 2781 | IT-FR = 1495 | -9085 | -9085 | -9085 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 598 | 0 | FR | 2500 | Bilateral - CREYS GENISSIAT 1
20231129 | November | 1430 |  | 7130 | 700 |  | 700 | 6619 | FR-IT = 2479 | IT-FR = 1495 | -9085 | -9085 | -9085 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 511 | 0 | FR | 2500 | Bilateral - CREYS GENISSIAT 1
20231129 | November | 1530 |  | 5022 | 2060 |  | 2060 | 4909 |  |  | 0 | 0 | 0 | GSK Limitation | Smoothing ramp | NA | 113 | 0 | Smoothing
20231129 | November | 1830 |  | 5584 | 1891 |  | 2042 | 5150 | FR-IT = 1310 | IT-FR = 1137 | 0 | 0 | 0 | GSK Limitation | Min import NTC Threshold | NA | 283 | 0 | FR | 2500 | Bilateral - CREYS GENISSIAT 1
20231129 | November | 1930 |  | 5499 | 1891 |  | 1891 | 5150 | FR-IT = 1310 | IT-FR = 1142 | 0 | 0 | 0 | GSK Limitation | Min import NTC Threshold | NA | 349 | 0 | FR | 2500 | Bilateral - CREYS GENISSIAT 1
20231129 | November | 2030 |  | 5584 | 1891 |  | 1891 | 5150 | FR-IT = 1310 | IT-FR = 1142 | 0 | 0 | 0 | GSK Limitation | Min import NTC Threshold | NA | 434 | 0 | FR | 2500 | Bilateral - CREYS GENISSIAT 1
20231130 | November | 1330 |  | 5867 | 95 |  | 95 | 5526 |  |  | 0 | 0 | 0 | ID schedules | Smoothing ramp | NA | 341 | 0 | Smoothing
20231130 | November | 1430 |  | 5867 | 98 |  | 98 | 4112 |  |  | 0 | 0 | 0 | GSK Limitation | Smoothing ramp | NA | 1755 | 0 | Smoothing
20231130 | November | 1830 |  | 3172 | 994 |  | 1201 | 1396 |  |  | 0 | 0 | 0 | GSK Limitation | Smoothing ramp | NA | 1569 | 0 | Smoothing
20231130 | November | 1930 |  | 3087 | 994 |  | 1200 | 2213 |  |  | 0 | 0 | 0 | GSK Limitation | Smoothing ramp | NA | 668 | 0 | Smoothing
20231201 | December | 1230 |  | 8328 | 2513 |  | 2513 | 7295 | FR-IT = 1942 | IT-FR = 1495 | -26194 | -26194 | -26194 | Critical Branch | Min import NTC Threshold | NA | 1033 | 0 | FR | 2500 | Bilateral - RDCR CREYS GENISSIAT 1
20231201 | December | 1330 |  | 8328 | 2513 |  | 2513 | 7295 | FR-IT = 1942 | IT-FR = 1495 | -26194 | -26194 | -26194 | Critical Branch | Min import NTC Threshold | NA | 1033 | 0 | FR | 2500 | Bilateral - RDCR CREYS GENISSIAT 1
20231201 | December | 1430 |  | 8328 | 2513 |  | 2513 | 7253 | FR-IT = 1921 | IT-FR = 1495 | -26194 | -26194 | -26194 | Critical Branch | Min import NTC Threshold | NA | 1075 | 0 | FR | 2500 | Bilateral - RDCR CREYS GENISSIAT 1
20231201 | December | 1530 |  | 8100 | 2513 |  | 2513 | 7295 | FR-IT = 1942 | IT-FR = 1495 | -20960 | -20960 | -20960 | TTC Selection - LTTC | Min import NTC Threshold | NA | 805 | 0 | FR | 2500 | Bilateral - RDCR CREYS GENISSIAT 1
20231201 | December | 1630 |  | 8100 | 2513 |  | 2513 | 7295 | FR-IT = 1942 | IT-FR = 1495 | -20960 | -20960 | -20960 | TTC Selection - LTTC | Min import NTC Threshold | NA | 805 | 0 | FR | 2500 | Bilateral - RDCR CREYS GENISSIAT 1
20231201 | December | 1730 |  | 8100 | 2513 |  | 2513 | 7295 | FR-IT = 1942 | IT-FR = 1495 | -20960 | -20960 | -20960 | TTC Selection - LTTC | Min import NTC Threshold | NA | 805 | 0 | FR | 2500 | Bilateral - RDCR CREYS GENISSIAT 1
20231201 | December | 1830 |  | 8100 | 1813 |  | 1813 | 7712 | FR-IT = 1942 | IT-FR = 1495 | -12375 | -12375 | -12375 | TTC Selection - LTTC | Min import NTC Threshold | NA | 388 | 0 | FR | 2500 | Bilateral - RDCR CREYS GENISSIAT 1
20231201 | December | 1930 |  | 8100 | 1813 |  | 1813 | 7712 | FR-IT = 1942 | IT-FR = 1495 | -12375 | -12375 | -12375 | TTC Selection - LTTC | Min import NTC Threshold | NA | 388 | 0 | FR | 2500 | Bilateral - RDCR CREYS GENISSIAT 1
20231201 | December | 2030 |  | 8100 | 1813 |  | 1813 | 7148 |  |  | -12375 | -12375 | -12375 | TTC Selection - LTTC | Smoothing ramp | NA | 952 | 0 | Smoothing
20231201 | December | 2130 |  | 8100 | 83 |  | 83 | 7389 | FR-IT = 2495 | IT-FR = 1495 | -8011 | -8011 | -8011 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | NA | 711 | 0 | FR | 2500 | Bilateral - RDCR CREYS GENISSIAT 1
20231201 | December | 2230 |  | 8100 | 113 |  | 113 | 7389 | FR-IT = 2500 | IT-FR = 1495 | -8011 | -8011 | -8011 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | NA | 711 | 0 | FR | 2500 | Bilateral - RDCR CREYS GENISSIAT 1
20231201 | December | 2330 |  | 7305 | 158 |  | 158 | 6778 | FR-IT = 2497 | IT-FR = 1660 | -7098 | -7098 | -7098 | TTC Selection - LTTC | TTC Validation phase - bilateral reduction | NA | 527 | 0 | FR | 2500 | Bilateral - RDCR CREYS GENISSIAT 1
20231202 | December | 1530 |  | 8047 | 3828 |  | 3418 | 2968 | FR-IT = 1118 | IT-FR = 2099 | 0 | 0 | 0 | GSK Limitation | Full import calculation and Min export NTC Threshold | NA | 5489 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1
20231202 | December | 1630 |  | 8047 | 3813 |  | 3418 | 3308 | FR-IT = 838 | IT-FR = 2099 | 0 | 0 | 0 | GSK Limitation | Full import calculation and Min export NTC Threshold | NA | 5134 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1
20231202 | December | 1730 |  | 8047 | 3828 |  | 3418 | 3228 | FR-IT = 666 | IT-FR = 2099 | 0 | 0 | 0 | GSK Limitation | Full import calculation and Min export NTC Threshold | NA | 5229 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1
20231202 | December | 1830 |  | 6150 | 1084 |  | 1162 | 4430 | FR-IT = 1048 | IT-FR = 956 | -6691 | -6691 | -6691 | Critical Branch | Full import calculation | NA | 1642 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1
20231202 | December | 1930 |  | 6065 | 1084 |  | 1084 | 4503 | FR-IT = 975 | IT-FR = 878 | -6595 | -6595 | -6595 | Critical Branch | Full import calculation | NA | 1562 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1
20231202 | December | 2030 |  | 6150 | 1084 |  | 1084 | 4491 | FR-IT = 987 | IT-FR = 878 | -6691 | -6691 | -6691 | Critical Branch | Full import calculation | NA | 1659 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1
20231203 | December | 1530 |  | 8773 | 902 |  | 853 | 6162 |  |  | -4305 | -4305 | -4305 | Critical Branch | Smoothing ramp | NA | 2660 | 0 | Smoothing
20231203 | December | 1630 |  | 8773 | 887 |  | 840 | 6608 | AT-IT = 124 | IT-AT = 100 | -4305 | -4305 | -4305 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 2212 | 0 | AT | 100 | Reduction because NTC over thermal limit on border
20231203 | December | 1730 |  | 8773 | 902 |  | 853 | 6514 | AT-IT = 223 | IT-AT = 100 | -4305 | -4305 | -4305 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 2308 | 0 | AT | 100 | Reduction because NTC over thermal limit on border
20231205 | December | 1230 |  | 7484 | 676 |  | 676 | 6279 | FR-IT = 2000 | IT-FR = 995 | -5085 | -5085 | -5085 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 1205 | 0 | FR | 2000 | Bilateral - Essais HVDC
20231205 | December | 1330 |  | 7484 | 676 |  | 676 | 6279 | FR-IT = 2000 | IT-FR = 995 | -5085 | -5085 | -5085 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 1205 | 0 | FR | 2000 | Bilateral - Essais HVDC
20231205 | December | 1430 |  | 7484 | 676 |  | 676 | 6279 | FR-IT = 2000 | IT-FR = 995 | -5085 | -5085 | -5085 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 1205 | 0 | FR | 2000 | Bilateral - Essais HVDC
20231205 | December | 1530 |  | 7690 | 707 |  | 707 | 6432 | FR-IT = 2000 | IT-FR = 995 | -273 | -273 | -273 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 1258 | 0 | FR | 2000 | Bilateral - Essais HVDC
20231205 | December | 1630 |  | 7690 | 707 |  | 707 | 6793 | FR-IT = 2500 | IT-FR = 995 | -273 | -273 | -273 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 897 | 0 | FR | 2000 | Bilateral - Essais HVDC
20231205 | December | 1730 |  | 8490 | 707 |  | 707 | 7233 | FR-IT = 2007 | IT-FR = 993 | -895 | -895 | -895 | Minimum Margin | TTC Validation phase - bilateral reduction | NA | 1257 | 0 | FR | 2000 | Bilateral - Essais HVDC
20231206 | December | 1230 |  | 4297 | 2302 |  | 1873 | 4287 | AT-IT = 92 | IT-AT = 85 | 0 | 0 | 0 | GSK Limitation | Min import NTC Threshold | NA | 439 | 0 | AT | -100000 | Reduction because NTC over thermal limit on border
20231206 | December | 1330 |  | 4297 | 2302 |  | 1591 | 4287 | AT-IT = 92 | IT-AT = 85 | 0 | 0 | 0 | GSK Limitation | Min import NTC Threshold | NA | 721 | 0 | AT | -100000 | Reduction because NTC over thermal limit on border
20231206 | December | 1430 |  | 4297 | 2302 |  | 742 | 4287 | AT-IT = 92 | IT-AT = 81 | 0 | 0 | 0 | GSK Limitation | Min import NTC Threshold | NA | 1570 | 0 | AT | -100000 | Reduction because NTC over thermal limit on border
20231206 | December | 1530 |  | 4912 | 2382 |  | 779 | 4823 |  |  | 0 | 0 | 0 | GSK Limitation | Smoothing ramp | NA | 1692 | 0 | Smoothing
20231206 | December | 1630 |  | 4912 | 2382 |  | 1043 | 4823 |  |  | 0 | 0 | 0 | GSK Limitation | Smoothing ramp | NA | 1428 | 0 | Smoothing
20231206 | December | 1730 |  | 5312 | 2382 |  | 1932 | 5233 |  |  | 0 | 0 | 0 | GSK Limitation | Smoothing ramp | NA | 529 | 0 | Smoothing
20231206 | December | 1830 |  | 6252 | 1362 |  | 1321 | 6001 | AT-IT = 240 | IT-AT = 80 | 0 | 0 | 0 | GSK Limitation | Validation phase | NA | 292 | 0 | AT | 85 | Reduction because NTC over thermal limit on border
20231206 | December | 1930 |  | 6252 | 1362 |  | 1283 | 5836 | AT-IT = 240 | IT-AT = 80 | 0 | 0 | 0 | GSK Limitation | Validation phase | NA | 495 | 0 | AT | 85 | Reduction because NTC over thermal limit on border
20231206 | December | 2030 |  | 6252 | 1362 |  | 1362 | 6179 | AT-IT = 240 | IT-AT = 80 | 0 | 0 | 0 | GSK Limitation | TTC Validation phase - bilateral reduction | NA | 73 | 0 | AT | 85 | Reduction because NTC over thermal limit on border
20231207 | December | 1230 |  | 6627 | 808 |  | 808 | 5678 | FR-IT = 2500 | IT-FR = 995 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 949 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1
20231207 | December | 1330 |  | 6627 | 808 |  | 808 | 5678 | FR-IT = 2500 | IT-FR = 995 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 949 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1
20231207 | December | 1430 |  | 6627 | 808 |  | 808 | 5678 | FR-IT = 2500 | IT-FR = 995 | 0 | 0 | 0 | ID schedules | TTC Validation phase - bilateral reduction | NA | 949 | 0 | FR | 2500 | Bilateral - RDCR CREYS - GENISSIAT 1
20231210 | December | 1230 |  | 7354 | 836 |  | 836 | 5624 | AT-IT = -100 | IT-AT = -100 | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | 1730 | 0 | AT | -100 | ATC blocked
20231210 | December | 1330 |  | 7354 | 836 |  | 836 | 5524 | AT-IT = -100 | IT-AT = -100 | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | 1830 | 0 | AT | -100 | ATC blocked
20231210 | December | 1430 |  | 7354 | 836 |  | 511 | 6298 | AT-IT = 225 | IT-AT = 225 | 0 | 0 | 0 | Scheduled TTC | TTC Validation phase - bilateral reduction | NA | 1381 | 0 | AT | -225 | ATC blocked
20231216 | December | 1530 |  | 11199 | 822 |  | 822 | 8533 |  |  | 0 | 0 | 0 | GSK Limitation | Smoothing ramp | NA | 2666 | 0 | Smoothing
20231216 | December | 1630 |  | 11199 | 822 |  | 822 | 9402 | FR-IT = 4177 | IT-FR = 1932 | 0 | 0 | 0 | GSK Limitation | Full import calculation | NA | 1797 | 0 | FR | 4485 | Bilateral - Process failed: missing input
20231216 | December | 1730 |  | 11199 | 822 |  | 822 | 9402 | FR-IT = 4177 | IT-FR = 1932 | 0 | 0 | 0 | GSK Limitation | Full import calculation | NA | 1797 | 0 | FR | 4485 | Bilateral - Process failed: missing input
20231223 | December | 1530 |  | 8443 | 907 |  | 907 | 6623 |  |  | -2885 | -2885 | -2885 | ID schedules | Smoothing ramp | NA | 1820 | 0 | Smoothing
20231223 | December | 1630 |  | 8443 | 907 |  | 907 | 7949 |  |  | -2885 | -2885 | -2885 | ID schedules | Smoothing ramp | NA | 494 | 0 | Smoothing
20231223 | December | 2130 |  | 9256 | 862 |  | 862 | 8451 | FR-IT = 1953 | IT-FR = 2160 | -4469 | -4469 | -4469 | Critical Branch | Full import calculation | NA | 805 | 0 | FR | 4485 | Bilateral - Process failed: missing input
20231223 | December | 2230 |  | 9256 | 907 |  | 907 | 8415 | FR-IT = 2246 | IT-FR = 2160 | -4469 | -4469 | -4469 | ID schedules | Full import calculation | NA | 841 | 0 | FR | 4485 | Bilateral - Process failed: missing input
20231223 | December | 2330 |  | 8573 | 941 |  | 941 | 7395 | FR-IT = 1235 | IT-FR = 2160 | -3796 | -3796 | -3796 | ID schedules | Full import calculation | NA | 1178 | 0 | FR | 4338 | Bilateral - Process failed: missing input
20231224 | December | 1830 |  | 4933 | 712 |  | 712 | 4843 | FR-IT = 1934 | IT-FR = 2160 | 0 | 0 | 0 | GSK Limitation | Full import calculation | NA | 90 | 0 | FR | 4338 | Bilateral - Process failed: missing input
20231224 | December | 1930 |  | 4933 | 712 |  | 712 | 4866 | FR-IT = 1915 | IT-FR = 2160 | 0 | 0 | 0 | GSK Limitation | Full import calculation | NA | 67 | 0 | FR | 4338 | Bilateral - Process failed: missing input
20231224 | December | 2030 |  | 4933 | 712 |  | 712 | 4866 | FR-IT = 1915 | IT-FR = 2160 | 0 | 0 | 0 | GSK Limitation | Full import calculation | NA | 67 | 0 | FR | 4338 | Bilateral - Process failed: missing input
20231224 | December | 2130 |  | 4215 | 938 |  | 938 | 4079 | FR-IT = 1953 | IT-FR = 2160 | 0 | 0 | 0 | GSK Limitation | Full import calculation | NA | 136 | 0 | FR | 4338 | Bilateral - Process failed: missing input
20231224 | December | 2330 |  | 3679 | 938 |  | 938 | 2957 | FR-IT = 1235 | IT-FR = 2160 | 0 | 0 | 0 | GSK Limitation | Full import calculation | NA | 722 | 0 | FR | 4338 | Bilateral - Process failed: missing input
20231225 | December | 1230 |  | 3062 | 1052 |  | 1052 | 2035 | FR-IT = -61 | IT-FR = 825 | 0 | 0 | 0 | GSK Limitation | Full import calculation | NA | 1027 | 0 | FR | 4338 | Bilateral - Process failed: missing input
20231225 | December | 1330 |  | 3062 | 1052 |  | 1052 | 1479 | FR-IT = -98 | IT-FR = 825 | 0 | 0 | 0 | GSK Limitation | Full import calculation | NA | 1583 | 0 | FR | 4338 | Bilateral - Process failed: missing input
20231225 | December | 1430 |  | 3062 | 1052 |  | 1052 | 1281 | FR-IT = 99 | IT-FR = 825 | 0 | 0 | 0 | GSK Limitation | Full import calculation | NA | 1781 | 0 | FR | 4338 | Bilateral - Process failed: missing input
20231227 | December | 1830 |  | 9176 | 907 |  | 907 | 6085 |  |  | -10207 | -10207 | -10207 | Critical Branch | Smoothing ramp | NA | 3091 | 0 | Smoothing
20231227 | December | 1930 |  | 9176 | 907 |  | 907 | 6838 | FR-IT = 3200 | IT-FR = 1995 | -10207 | -10207 | -10207 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 2338 | 0 | FR | 3200 | Bilateral - Outage of Grande Ile - Piossasco 2
20231227 | December | 2030 |  | 9176 | 907 |  | 907 | 6962 | FR-IT = 3125 | IT-FR = 1995 | -10207 | -10207 | -10207 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 2214 | 0 | FR | 3200 | Bilateral - Outage of Grande Ile - Piossasco 2
20231227 | December | 2130 |  | 7485 | 907 |  | 907 | 6938 | FR-IT = 3200 | IT-FR = 1995 | -7631 | -7631 | -7631 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 547 | 0 | FR | 3200 | Bilateral - Outage of Grande Ile - Piossasco 2
20231227 | December | 2230 |  | 7485 | 907 |  | 907 | 6938 | FR-IT = 3200 | IT-FR = 1995 | -7631 | -7631 | -7631 | Critical Branch | TTC Validation phase - bilateral reduction | NA | 547 | 0 | FR | 3200 | Bilateral - Outage of Grande Ile - Piossasco 2
20231227 | December | 2330 |  | 6802 | 942 |  | 942 | 6237 | FR-IT = 3003 | IT-FR = 2160 | -6713 | -6713 | -6713 | Critical Branch | Full import calculation | NA | 565 | 0 | FR | 3200 | Bilateral - Outage of Grande Ile - Piossasco 2
20231229 | December | 1530 |  | 8910 | 696 |  | 696 | 5148 |  |  | -6803 | -6803 | -6803 | Critical Branch | Smoothing ramp | NA | 3762 | 0 | Smoothing
20231229 | December | 1630 |  | 8910 | 696 |  | 696 | 6505 |  |  | -6803 | -6803 | -6803 | Critical Branch | Smoothing ramp | NA | 2405 | 0 | Smoothing
20231229 | December | 1730 |  | 8910 | 696 |  | 696 | 7339 | FR-IT = 3200 | IT-FR = 1995 | -6803 | -6803 | -6803 | Critical Branch | Full import calculation | NA | 1571 | 0 | FR | 4485 | Bilateral - Process failed: missing input
20231231 | December | 1230 |  | 4634 | 938 |  | 938 | 4534 | FR-IT = 2246 | IT-FR = 2160 | 0 | 0 | 0 | GSK Limitation | Full import calculation | NA | 100 | 0 | FR | 4338 | Bilateral - Process failed: missing input
20231231 | December | 1330 |  | 4634 | 938 |  | 938 | 4534 | FR-IT = 2246 | IT-FR = 2160 | 0 | 0 | 0 | GSK Limitation | Full import calculation | NA | 100 | 0 | FR | 4338 | Bilateral - Process failed: missing input
20231231 | December | 1430 |  | 4634 | 938 |  | 938 | 4534 | FR-IT = 2246 | IT-FR = 2160 | 0 | 0 | 0 | GSK Limitation | Full import calculation | NA | 100 | 0 | FR | 4338 | Bilateral - Process failed: missing input

## ID FLAGS processing
TSO | Long description | Short | Type | # of TS
CH | Expected overloading on the following CNEC: CNE: 380kV Gorlago - Robbia , C: N-1 SOAZZA-BULCIAGO | CNE: 380kV Gorlago - Robbia , C: N-1 SOAZZA-BULCIAGO | Overload | 9
CH | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE | CNE: 220kV Riddes - Valpelline , C: N-2 ALBERTVILLE-RONDISSONE | Overload | 18
CH | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA | CNE: 380kV Fiorano-Robbia [DIR][IT], C: 380KV GORLAGO-ROBBIA | Overload | 2
CH | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | Overload | 5
CH | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 Pradella-Robbia + Filisur-Robbia | Overload | 1
CH | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV GORLAGO-ROBBIA | Overload | 7
CH | Expected overloading on the following CNEC: CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV SILS-SOAZZA | CNE: 380kV Fiorano-Robbia [DIR] [CH], C: 380KV SILS-SOAZZA | Overload | 1
CH | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 ALBERTVILLE-RONDISSONE 1 | CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-1 ALBERTVILLE-RONDISSONE 1 | Overload | 1
CH | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | CNE: 380kV Lavorgo - Musignano [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | Overload | 1
CH | Expected overloading on the following CNEC: CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | CNE: 220kV Riddes - Valpelline [DIR] [CH], C: N-2 ALBERTVILLE-RONDISSONE | Overload | 8
CH | Expected overloading on the following CNEC: CNE: 380kV Fiorano - Robbia , C: 380KV GORLAGO-ROBBIA | CNE: 380kV Fiorano - Robbia , C: 380KV GORLAGO-ROBBIA | Overload | 4
CH | IT issues in internal Validation Tool. BackUp-NTC-values are applied. |  | Fault | 11
CH | Missing CNEC in CC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE |  | Missing CNEC in CC | 2
CH | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 ALBERTVILLE-RONDISSONE | CNE: 380kV Bulciago - Soazza , C: N-2 ALBERTVILLE-RONDISSONE | Overload | 1
CH | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Pradella-Robbia + Filisur-Robbia | CNE: 380kV Bulciago - Soazza , C: N-2 Pradella-Robbia + Filisur-Robbia | Overload | 5
CH | Expected overloading on the following CNEC: CNE: 380kV Fiorano - Robbia , C: N-2 ALBERTVILLE-RONDISSONE | CNE: 380kV Fiorano - Robbia , C: N-2 ALBERTVILLE-RONDISSONE | Overload | 1
CH | Expected overloading on the following CNEC: CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | CNE: 380kV Bulciago - Soazza , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | Overload | 40
CH | Expected overloading on the following CNEC: CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE | CNE: 220kV Pallanzeno - Serra , C: N-1 AIROLO-FIESCH/PONTE | Overload | 1
CH | Expected overloading on the following CNEC: CNE: 380kV Filisur - Sils , C: 380KV GORLAGO-ROBBIA | CNE: 380kV Filisur - Sils , C: 380KV GORLAGO-ROBBIA | Overload | 1
CH | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 Pradella-Robbia + Filisur-Robbia | CNE: 380kV Lavorgo - Musignano , C: N-2 Pradella-Robbia + Filisur-Robbia | Overload | 5
CH | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | CNE: 380kV Lavorgo - Musignano , C: N-2 Robbia-Gorlago + Robbia-S.Fiorano | Overload | 6
CH | Reduction due to the following overloaded element(s): N-2 380kV Pradella-Robbia + Filisur-Robbia : 380kV Sils-Soazza |  | Overload | 3
CH | Reduction due to the following overloaded element(s): N-2 380kV Albertville-Rondissone 1 + 2 : 220kV Avise-Riddes |  | Overload | 3
CH | Expected overloading on the following CNEC: CNE: 380kV Lavorgo - Musignano , C: N-2 ALBERTVILLE-RONDISSONE | CNE: 380kV Lavorgo - Musignano , C: N-2 ALBERTVILLE-RONDISSONE | Overload | 1
FR | Bilateral - Process failed: missing input |  | Fault | 17
FR | Bilateral - Outage of Grande Ile - Piossasco 2 |  | Outage | 5
FR | Bilateral - RDCR CREYS GENISSIAT 1 |  | Outage | 11
FR | Bilateral - Essais HVDC |  | Outage | 6
FR | ATC blocked |  | ATC blocked | 7
FR | Process fail during TSO validation phase |  | Fault | 3
FR | Bilateral - N-2 Alberville-Rondissone / Cornier-Riddes-St-Triphon |  | Outage | 9
FR | Bilateral - N-1 Creys - Genissiat |  | Outage | 8
FR | Bilateral - RDCR CREYS - GENISSIAT 1 |  | Outage | 15
FR | Bilateral - RDCR B.TOLLOT-GENISSIAT et CREYS-GENISSIAT |  | Outage | 9
FR | Bilateral - N-2 ALBERTVILLE-GRANDE ILE sur CREYS-GENISSIAT 2 |  | Outage | 6
FR | Bilateral - N-2 ALBERTVILLE - RONDISSONE |  | Outage | 9
FR | Bilateral - RDCR CORNIER GENISSIAT |  | Outage | 6
FR | Bilateral - N-2 ALBERTVILLE G.ILE |  | Outage | 3
FR | Bilateral - N-2 Albertville Rondissone / Albertville-Grande Ile |  | Outage | 10
FR | Bilateral - N-2 Albertville-Rondissonne / Albertville - Grande-Ile |  | Outage | 9
FR | Bilateral - N-2 Albertville-Rondissonne / Albertville-G.Ile |  | Outage | 1
FR | Bilateral - N-2 Albertville-Rondissonne / Albertville - G.Ile |  | Outage | 4
FR | Bilateral - n-2Albertville Grand ile |  | Outage | 3
FR | Bilateral - N-2 ALBERTVILLE-RONDISSONE/CREYS-GENISSIAT |  | Outage | 9
FR | Bilateral - Probleme coordination Terna |  | Fault | 9
FR | Bilateral - N-2 ALBERVILLE G.ILE / CREYS GENISSIAT 1 |  | Outage | 9
Smoothing |  |  | Smoothing | 29
Fictive flag |  |  | Fictive flag | 11
AT | ATC blocked |  | ATC blocked | 3
AT | Because of high redispatch the leftover intraday capacity was set to 0 |  | Redispatch | 12
AT | Reduction because of outage of line 912 |  | Outage | 8
AT | Bilateral - Because of high redispatch the leftover intraday capacity was set to 0 |  | Redispatch | 9
AT | Bilateral - Reduction because of outageof line 912 |  | Outage | 2
AT | Reduction because NTC over thermal limit on border |  | NTC over thermal limit | 63
AT | Bilateral - Reduction becauseof disconnection of line 912 % 261 |  | Outage | 1
AT | Bilateral - Reduction because NTC over thermal limit on border |  | NTC over thermal limit | 17
AT | Bilateral - Reduction because of disconnection of line 261 & 912 |  | Outage | 1
FR | Bilateral - CREYS GENISSIAT 1 |  | Outage | 6