Annex II – Core TSOs general measures and action plan to avoid future cross-zonal capacity reductions

Q3 2025

Table of Contents

Introduction	2

1.	CEPS	4

2.	DAVinCy TSOs	4

2.1.	APG	5

2.2.	German TSOs	5

2.3.	TENNET TSO BV	6

3.	ELES	7

4.	ELIA	8

5.	HOPS	8

6.	MAVIR	9

7.	PSE	10

8.	RTE	11

9.	SEPS	11

10.	Transelectrica	13

# Introduction

According to Articles 20(14)(b) and 20(15) of the DA CCM, Core TSOs have the obligation to provide general measures and/or action plans in order to avoid cross-zonal capacity reductions in the future, as follows:

- As per Article 20(14)(b): General measures to avoid cross-zonal capacity reductions in the future

- As per Article 20(15): When a given Core TSO reduces capacity for its CNECs in more than 1% of DA CC MTUs of the analysed quarter, the concerned TSO shall provide to the CCC a detailed report and action plan describing how such deviations are expected to be alleviated and solved in the future.

This annex contains the required information described above for each Core TSO that has applied capacity reductions for at least 1 DA CC MTU of the analysed quarter.

# CEPS

1.1 General measures to avoid cross-zonal capacity reductions in the future, as per Art. 20(14)(b) of DA CCM

ČEPS has implemented the following measures to avoid cross-zonal capacity reduction. Firstly, in its individual validation, only technically feasible scenarios (a set of Core NPs) are tested. These scenarios reflect know-how about max/min generation capabilities of BZs, and popular flow directions. As a result, the tested MCP (NPs vector) is not only an extreme utilization of the domain (vertex) but also a realistic grid situation. This leads to highly efficient IVA applications. Secondly, a wide variety of remedial actions are considered in the ČEPS optimization algorithm. This helps ČEPS to efficiently eliminate the majority of the operational security threats without cross-zonal capacity reduction. Finally, by applying IVA directly to the over-congested element, the minimal value of IVA required is guaranteed.

1.2 Detailed report and action plan describing how such deviations are expected to be alleviated and solved in the future

ČEPS reduced capacity in Q3 2025 for its CNECs during the Individual validation in 104 cases, e.i, in 46 distinct MTUs (approximately 2 % of DA CC MTUs of the analysed quarter). This represents the first quarter since the Core FB MC go-live in June 2022, when the threshold of 1 % MTUs with IVA application was exceeded by ČEPS.

Please find below an explanation and proposed alleviation of this exceptional situation.

The analysed 104 cases were not equally distributed during Q3 2025, but occurred in the period from 25th September. See the table below:

| BD | Number of IVA applications |
| --- | --- |
| 18.08 | 1 |
| 25.09 | 65 |
| 26.09 | 23 |
| 27.09 | 10 |
| 28.09 | 3 |
| 29.09 | 2 |

This corresponds with the exceptional grid situation during this period. There are two 400 kV cross-zonal lines between the CZ and AT bidding zones, namely V437 Slavetice – Dürnrohr and V438 Slavetice – Dürnrohr. V437 Slavetice – Dürnrohr was in planned outage from 1.9.2025 till 24.10.2025, and V438 Slavetice – Dürnrohr was in planned outage from 25.9.2025 till 9.10.2025. (Due to maintenance and partial upgrade.) Which means that during the period from 25.9.2025 till 9.10.2025, there was no 400 kV connection between the CZ and AT bidding zones.

As a result, all the market flows in the highly in-demand direction from Western Europe to Southeast Europe were transferred in parallel lines. These were the 200 kV cross-zonal lines between CZ and AT, as well as all the cross-zonal lines at the CZ-SK border. The grid situation can be seen in the following picture (blue – lines in planned outage, red – lines with IVA application).

Picture: Grid situation 25.9.2025 - 9.10.2025 (blue – lines in planned outage, red – lines with IVA applied)

Although all the expected available remedial actions were optimized, for multiple MTUs the IVA had to be applied to ensure operational security. For the following CNECs IVA was applied most frequently: [CZ-SK] Nosovice – Varin / N-1 Sokolnice – Stupava, [CZ-AT] Sokolnice - Zaya - V244 / N-1 Sokolnice - Zaya V243, [CZ-AT] Sokolnice - Zaya - V243 / N-1 Sokolnice - Zaya V244.

Already during the analyzed period, ČEPS has applied multiple measures to minimize the negative impact of the grid situation on the cross-zonal capacities. This comprised the D2CF vs DACF ex-post risk assessment, that resulted in update of Individual Validation Tool parameters. Furthermore, extra time for operators to perform the individual validation was given. As a result, IVA application could be reduced even further after few days of the outage, see the table above. However, more frequent IVA applications continued till the end of the outage period (9.10.2025) and will be part of the Q4 2025 reporting as a result.

In our understanding, it is an expected outcome that during such a major outage period, a strain is put on all the remaining grid elements, especially the remaining cross-zonal elements.  In other words, it is expected that a simultaneous outage of multiple 400 kV cross-zonal lines will lead to a decrease in cross-zonal capacities

# DAVinCy TSOs

In order to provide a better understanding of the results and the processes applied among DAVinCy TSOs, following are some introductory explanations:

APG, Tennet NL and the German TSOs (DAVinCy TSOs) use a common tool for individual validation called DAVinCy (Day Ahead Validation of Capacity). In case an overload cannot be solved with the available remedial actions, DAVinCy determines the necessary Individual Validation Adjustments (IVAs) on relevant CNECs with the objective to minimise the overall capacity reduction among the six DAVinCy TSOs. This can lead to situations where an overload occurs in one control area of TSO A whereas the IVA(s) is/are applied within other control areas, e.g., of TSOs B and C.

The application of an IVA prevents a network element from being overloaded and does not necessarily lead to a deviation from the minimum cross-zonal capacity according to Article 16(8) of regulation (EU) 2019/943 on the internal market of electricity.

In the opinion of the DAVinCy TSOs, the cooperation of six TSOs within the DAVinCy consortium leads to a very effective result when relieving potential overloads within the grid in order to secure operational security. This is caused by the fact that remedial actions within six control areas can be used. Moreover, IVAs having a minimal impact on cross-zonal capacities offered to the market can be applied to solve congestions. Furthermore, the DAVinCy TSOs acknowledge, that this report has to be based on the amount of capacity reductions, i.e. IVAs applied by DAVinCy. Nevertheless, it should be noted, that measures to reduce the application of IVAs need to address the cause of IVAs, respectively the reduction of congestions and fallbacks.

The DAVinCy TSOs plan to apply the following measures in order to minimize the application of IVAs and, as required by Article 20(14)(b) and Article 20(15) DA CCM, avoid cross-zonal capacity reductions in the future:

Further improvement of process robustness through the use of redundant IT systems, plausibility checks and replacement strategies for input data, separate systems for test and productive environment and implementation of security management.

Improvement of automated topology optimization

Consideration of further cross-border redispatch with neighbouring countries

Increase of regional granularity of RES redispatch

## APG

The application of an IVA prevents a network element from being overloaded and does not necessarily lead to a deviation from the minimum cross-zonal capacity according to Article 16(8) of regulation (EU) 2019/943 on the internal market of electricity. Deviations from the minimum cross-zonal capacity according to the Austrian action plan, will be reported and reflected accordingly in the Austrian action plan report submitted to the Austrian NRA E-Control.

Ongoing developments and improvements of the tool by the DAVinCy TSOs in the recent years have already improved its performance and lead to a decrease in the amount of IVAs applied on their CNECs. APG fully supports the innovative functioning of DAVinCy since it increases the overall benefit of the Core region compared to a purely national individual validation and could be used as blueprint for an effective coordinated validation approach among all Core TSOs.

In Q3/2025, the following could be observed:

- In 46 hours or 2.08% of all MTUs in Q3/2025 an IVA was applied on a network element of APG.

- Out of these hours, in 24 hours or 1.09% of all MTUs in that quarter IVAs were applied to prevent potential overloads in the Austrian control area.

- Of the overall 46 hours, in 20 hours IVAs were applied as fallback due to a failure of the DAVinCy tool on a single business day.

The technical issue that led to the failure of the DAVinCy tool and led to a fallback application has already been resolved and implemented in the current version of DAVinCy.

In addition to improvements of the individual validation process and DAVinCy itself, APG plans to implement further measures according to the Austrian Action Plan. Those measures include, but are not limited to:

- Network reinforcement and optimisation, e.g. dynamic line rating to relieve grid elements with overloads in the future.

- Network expansion and planned infrastructure projects according to the Network Development Plan.

## German TSOs

The application of an IVA prevents a network element from being overloaded and does not necessarily lead to a deviation from the minimum cross-zonal capacity according to Article 16(8) of regulation (EU) 2019/943 on the internal market of electricity. In case of a deviation from the minimum cross-zonal capacity, the compliance with the minimum cross-zonal capacity targets of the German action plan according to the monitoring methodology approved by the German NRA Bundesnetzagentur is subject to the regulatory scrutiny. This is done by an approval of the report of German TSOs on available cross-zonal capacity for the year 2023.

Ongoing developments and improvements of the tool by the DAVinCy TSOs in the recent years have already improved its performance and lead to a decrease in the amount of IVAs applied on their CNECs. German TSOs fully support the innovative functioning of DAVinCy since it increases the overall benefit of the Core region compared to a purely national individual validation and could be used as blueprint for an effective coordinated validation approach among all Core TSOs.

Please note, that all German TSOs exceeded the 1-%-IVA threshold in Q3 2025 and are thus obligated to provide more details in this annex.

In Q3/2025, the following could be observed:

In 57 hours or 2.6 % of the MTUs an IVA was applied within the DAVinCy area.

In 44 hours or 2.0 % of the MTUs an IVA was applied on a network element of a German TSO.

Out of these hours, in 24 hours or 1,09% of the MTUs an IVA was applied as fallback due to a failure of the DAVinCy tool on a single business day. When excluding the fallback MTUs, no German TSO applied IVA in more than 1% of the MTUs.

Out of the remaining 20 hours without fallback, only in 13 hours or 0.6 % of the MTUs an overload within the control area of a German TSO was leading to an IVA application during the DAVinCy process.

The above-mentioned statistic shows that the amount of IVAs applied on a network element of a German TSO only exceeds the 1%-threshold by a relatively insignificant margin and only due to a single occurrence of fallback. For further reductions Amprion, respectively the German TSOs, depend on technical improvements to prevent DAVinCy fallbacks. The technical issue that led to the failure of the DAVinCy tool and lead to a fallback application on 24 MTUs has already been resolved and implemented in the current version of DAVinCy.

In addition to the measures mentioned in the general section for all DAVinCy TSOs, the planned grid enforcements within the control areas of the German TSOs will relieve grid elements with overloads in the future (cf. Action Plan of Germany and Network Development plan) will minimize the application of IVAs and, as required by Article 20(14)(b) and Article 20(15) DA CCM, avoid cross-zonal capacity reductions in the future.

## TENNET TSO BV

During the third quarter of 2025 TTN applied IVAs to avoid situations for which no measures in real time would be available. Although IVAs reduce the RAM on a CNEC, it does not necessarily end up in a violation of the minimum RAM available for cross zonal trade. Specifically, for the third quarter of 2025 the application of IVAs can be summarized as follows:

- For 1.18% of MTUs (26 hours) IVA was applied on pre-solved Dutch CNECs of the final FB domain

- In 24 hours or 1.09 % of the MTUs an IVA was applied as fallback

- For 5 MTUs IVA was applied on CNECs that were active constraints during the market coupling.

- The average IVA as % of Fmax over all affected MTUs was 3.41 %.

General measures to avoid cross-zonal capacity reductions in the future (Art. 20(14)(b) of DA CCM) are for TTN the following:

- Implementation of DLR on multiple lines.

- Grid reinforcement projects will increase thermal capacities in the long term.

# ELES

General measures to avoid cross-zonal capacity reductions in the future, as per Art. 20(14)(b) of DA CCM

Improvement in congestion management – we will continue to improve the quality of our inputs for CORE DA CC in order to avoid unnecessary IVA application in case of errors in inputs files.

Network development and optimisation

Detailed report and action plan describing how such deviations are expected to be alleviated and solved in the future

In the third quarter of 2025, ELES applied reduction for 3,4 % of MTU. There are three main reasons for this:

Presence of two CCR: The main reason for reduction at ELES is the fact, that we are in the cross-road of two CCR, which both aim to maximise capacities in order to fulfil 70% criteria. Often, maximisation of the capacities in Italy North CCR have negative effect on the RAM of Slovenian elements in CORE CCR. This is mostly due to the fact, that we have a PST on the Slovenian – Italian border, that is used to maximise Italy North NTC values.

Network weaknesses – there are some weaknesses on our network, most critical are the lines Podlog – Obersielach (SI-AT) and Divaca – Pehlin (SI - HR) - for both, the most reductions were applied.

Our plan to improve the situation consists of the following:

Additional training of operators and improvement of the local validation tool in order to improve the process and improve stability and reliability of the tool

Analysis will be performed on accuracy of validation tool (e.g. comparing the flows considered during the validation and realised flows). Based on the result of the analysis, the validation tool reliability margin will be adjusted in order to decrease the level of IVA application.

Network development and optimisation - For the Podlog – Obersielach line, we are in the process to obtain and install a static serous synchronous compensator (SSSC) in order to be able to relieve the flow on the element. SSSC is expected to be installed until the end of 2026. 
For the Divaca – Pehlin line, we are still investigation different possibilities to increase capacities (SSSC or high temperature lines).

# ELIA

General measures include, but are not limited to:

A daily follow up plus short-term mitigations and long-term local validation of the tool has been set up to improve the tool aiming to:

reduce the number of occurrences of fallbacks,

reduce the number of occurrences of spanning by switching to DCLF when no ACLF converges,

reduce the number of occurrences of excessive IVA application due to failure in the derogation step.

Congestion management through the shifting of overloads from the congested element to other CNECs via PST optimization to reduce the overall overloads, this action is already in place.

Common Core action ongoing to correct the DCimbalance corrected and the CGM used in the FB DA CC process to make the flowbased calculations more correct.

Temporary structural situation:

The nuclear phase out planned in Belgium is going to decrease the congestion around Doel and Mercator which are the most congested area. There is no additional action plan concerning these IVAs.

Situation linked to short outages:

There are no extra investments foreseen to cover N-2 situations like for temporary short outages.

# HOPS

General measures to avoid cross-zonal capacity reductions in the future, as per Art. 20(14)(b) of DA CCM

General measures include, but are not limited to:

Network development and optimisation

The goal is to increase the transmission capacity and reduce grid congestion. The measures to achieve these goals include strengthening the optimising the existing network and the development of new infrastructure.

Improvements concerning congestion management

Core CCR coordinated improvements based on shared forecasts and aligned assumptions in capacity calculations with coordinated actions to increase cross-zonal capacities and reduce uncertainties (CGM improvements, Coordinated validation, etc.). Also, inclusion of third countries could open further opportunities for HOPS (with planning process and implementation of remedial measures). Unscheduled allocated flows coming from commercial exchanges outside the Core CCR (Fuaf) has a strong impact on HOPS grid.

Detailed report and action plan describing how such deviations are expected to be alleviated and solved in the future

In the analysed quarter (Q3 2025), HOPS applied reduction to around 39% MTUs. For most MTUs, the reductions are applied to:

TL 220 kV Pehlin – Divača (36,6% MTUs, or around 84,9% of times of all applied reductions) with an associated contingency case TL 400 kV Melina - Divača.

TL 220 kV Zakučac - Mostar (2,1% MTUs, or around 4,8% of times of all applied reductions) without an associated contingency case.

TL 400 kV Tumbri – Krško 1 (0,8% MTUs, or around 1,9% of times of all applied reductions) with an associated contingency case TL 400 kV Tumbri – Krško 2.

TL 400 kV Tumbri – Krško 2 (0,8% MTUs, or around 1,9% of times of all applied reductions) with an associated contingency case TL 400 kV Tumbri – Krško 1.

Applied reductions on network element are mostly low (less than 8% of Fmax), while for several MTUs during August (BD20250821-22) higher values are applied on TL 220kV Pehlin - Divača due to unsolvable overloads in the relevant grid area caused by unavaliability of grid elements, additionally under the influence of high exchanges between Core and non-Core countries (impact of uncoordinated flows coming from third countries, mainly from the direction of RS and BA). Such reductions are planned to be solved by developing and optimising the transmission network.

In Q2 of 2025, HOPS installed HTLS conductors on TL 220 kV Brinje – VE Pađene that increases its maximum admissible power flow and improves available capacities.

Also, following the ongoing investigation of various options for increasing capacity for the TL 220 kV Pehlin – Divača, it is planned to start installing HTLS conductors on TL 220 kV Pehlin – Divača in Q4 2026.

Since HOPS is surrounded by two non-Core countries with a strong influence of non-coordinated flows, any deviation from the target NP can create an overloadings with potential security risks. These flows are taken into account within the CGM with an influence on the final available margin (RAM), while during validation HOPS should guarantee available capacities of the internal grid affected by the exchanges between Core (Central) Europe and Western Balkan and/or SEE region. Since RCCs create CGMs with the net postion forecast (NPF) modelling, we expect that with NPF evolution and the increase of the quality of the D2CF CGMs deviations and uncertainties between forecast and realised power flows will be minimized, especially deviations of non-Core countries that are currently based on D-1 NPs.

Improvements are also expected with upcoming important processes such as coordinated validation capacities and Regional Operational Security Coordination.

# MAVIR

- Explanation for the reductions applied by MAVIR in Q3, 2025

MAVIR performs the individual validation with the basic principle of determining CBCOs that can be potentially overloaded by a realistic market outcome. In case a CBCO which cannot be solved by available remedial actions from contingency analysis but selected to be potentially overloaded is identified, IVA with the objective of minimizing the loss of the flow-based domain volume is optimized and calculated in order to relieve the potential overload. In Q3, there were 54 business days with IVA applied to CBCOs by MAVIR due to two different factors. One is the pattern of significant power flows from import direction combined with strong transit flows from north-west to south-east and vice-versa. The hours with strong transit flows can be further exacerbated with planned special grid outage situation for which there is no other solution, but IVA application. The other factor that contributes to IVA is the application of fallback due to no solution from the optimization algorithm.There were 521 distinct hours (or 23.60% of the 2208 MTUs) with IVA application. There were 113 distinct hours with operational fallback IVA application which contributed to the amount of IVA in Q3. In total, 496 distinct hours, the CBCOs with IVAs were a domain limiting constraint. In total, there were 188 hours with active HU constraints, out of which there were 109 hours with non-zero IVA with the highest shadow price equal to 597 EUR/MW. There were 25 hours which did not fulfil the 20% minimum RAM requirement.

MAVIR aims to apply the following measures in order to minimize the application of IVAs and, as required by article 20(14)(b) and 20(15) DA CCM, avoid cross-zonal capacity reductions in the future:

- Consideration of effective topological remedial actions even for those hours in which the NRAO did not select them due to loopflow constraint violation, but the selection of RA would have mitigated the application of IVA amount.

Based on growing operational experience, methodological improvement in the IVA calculation by excluding areas of the domain in which the concerned overloaded element to the amount of IVA is less sensitive. Note that the operational experience also shows better judgement of IVA applications as to the trade-off between operational security and offered capacities.

There are several internal projects and cross-border projects planned with Slovakia, Romania and Serbia to further increase capacities available for the commercial cross-border trades in the day-head and intraday market timeframes. The planned cross-border investments by 2030 are the following, all included in TYNDP 2024:

- Second circuit of the 400 kV OHL Sajoivanka (HU) – Rimavská Sobota (SK) – (2028)

  - This grid investment should help to reduce the frequency of 70%minRAM non-fulfilment for [SK-HU] Levice – God [DIR] [HU] and [SK-HU]  R. Sobota – Sajoivanka [DIR] [HU] cross-border CNEC

- New 400 kV OHL Debrecen Del (HU) - Oradea Sud (RO) – (2030)

  - This grid investment should help to reduce the frequency of 70%minRAM non-fulfilment for the [RO-HU] Arad – Sandorfalva [OPP] [HU] cross-border CNEC

- Second circuit of the 400 kV OHL Nadab (RO) - Bekescsaba (HU) – (2028)

  - This grid investment should help to reduce the frequency of 70%minRAM non-fulfilment for the [RO-HU] Arad – Sandorfalva [OPP] [HU] cross-border CNEC

- New 400 kV OHL SS Subotica 3 (RS) – SS Sandorfalva (HU) – (2028)

  - This grid investment should help to reduce the frequency of 70%minRAM non-fulfilment for the [RO-HU] Arad – Sandorfalva [OPP] [HU] cross-border CNEC

In addition to the cross-border investments, the following internal investments are expected to have a significant effect on cross-zonal trade:

- New 400 kV OHL between Sandorfalva and Szolnok, replacing the existing 220 kV line (2028)

  - This gird investment should help to reduce the frequency of 70%minRAM non-fulfilment on [HU-HU] Paks – Sandorfalva [DIR]. The [HU-HU] Szolnok – Szeged network element will be decommissioned.

- Second 400 kV OHL between Felsozsolca and Sajoivanka (2026)

  - This gird investment should help to reduce the frequency of 70%minRAM non-fulfilment for [SK-HU] Levice – God [DIR] [HU] cross-border network element and [HU-HU] Felsozsolca – Sajoivanka [OPP] [HU] network element.

It is important to note that there are also internal and cross-border grid development projects in Slovakia which are foreseen to considerably mitigate grid constraints over the SK – HU.

- Planned development in the Velky Dur – Levice region (2029)

  - This grid investment should help to largely reduce the most frequently limiting constraints [SK-SK] V. Dur – Levice 1 [DIR] and [SK-SK] V. Dur – Levice 2 [DIR] from the Top 20 ATC limiting element list. It isl also foreseen to help to mitigate the grid constraints over the SK – HU border

Although MAVIR provides already today a high level of RAM on most of its CNECs in the day-ahead timeframe on several network elements, the RAM may be limited to maintain operational security. For an increase of the RAM the key is the improvement of security coordination in the Core CCR with the implementation of coordinated validation and ROSC.

# PSE

General measures to avoid cross-zonal capacity reductions in the future, as per Art. 20(14)(b) of DA CCM:

PSE is taken under consideration: long-, medium- and short-term measures to prevent capacity reduction.

Generally, the main source of improvements will be grid developments, as prescribed in the Action Plan and as foreseen in the Grid Development Plan.

In medium PSE is investigating dynamic monitoring of the lines, which increase the line rating.

As the short-term measures, PSE implemented parametrization of the validation tool, which potentially leading to avoiding application of low IVA values (so that IVAs will be less frequent).  Additional propose was to include in individual validation topological remedial actions.

In some cases the IVA was implemented in specific maintenance situation, this will be only temporary and additional investigation are not foreseen,

2.

Detailed report and action plan describing how such deviations are expected to be alleviated and solved in the future.

In the analysed quarter (Q3 2025), PSE applied reduction of ~1,4% MTUs = 31 distinct MTUs with applied reductions. In total it was 89134MW of IVA. All reductions were applied as outcome of individual validation.

In the analysed quarter (Q3 2025), for most MTUs, the reductions are applied mostly to:

CNE Krajnik-Vierraden c.1 PSE applied 68434MW of IVA (~77,% of total reductions applied as outcome of individual validation tool), mainly due to influence of planned outages. Second reason is high F0Core, even ~123%Fmax.

CNE PST and Tielines from Mikulowa station PSE applied 17013MW of IVA (~19% of total reductions applied as outcome of individual validation tool), mainly due to influence of planned outages. Second reason is high F0Core, even ~68%Fmax.

Wielopole - Nosovice PSE applied 1385MW of IVA (~1,5% of total reductions applied as outcome of individual validation tool). Applied reducions results mailny from the planned outage in considered area. Second reason is high F0Core, even ~71%Fmax.

Only one day 2025.09.25 PSE applied 81196MW of IVA. Main reason is extreme high F0_Core. Max F0_Core in this day was ~123% of Fmax

Action plan:

Reinforcement of the grid is included in grid development plan like construction of the 400 kV Baczyna-Plewiska line and Construction of the 400/220/110 kV Baczyna substation together with connection of the 400 kV Krajnik-Plewiska line and 220 kV Krajnik-Gorzów line (planned in 2026), Upgrade of the 400 kV Rzeszów-Krosno Iskrzynia line (planned in 2026)

Monitoring of CGM quality in case of F0_Core. This is a very important element, for which unfortunately PSE is not able to do much, since CGM quality results from modelling issues from power systems outside of PSE.

Increasing the accuracy of built IGM models. Implemented on an ongoing basis.

# RTE

RTE is currently improving its validation tool by integrating a RAO function, which will allow for finer tailoring of the IVAs.

The release of this new version is planned for Q4 2025 / Q1 2026.

# SEPS

During the third quarter (Q3) of 2025, the Individual Validation Adjustment (IVA) was applied in 20.56% of all Market Time Units (MTUs). The primary drivers behind the implementation of IVA during this period were elevated forecasted transit flows and several planned outages on critical transmission network elements. Notably, a significant portion of these reductions stemmed from constraints on the following interconnectors and domestic lines:

[SK-HU] Levice – Gönyű [DIR] [SK] + N-1 Rimavská Sobota – Sajóivánka

[SK-SK] Veľký Ďur – Levice 1 [DIR] + N-1 Veľký Ďur – Levice 2

[SK-SK] Veľký Ďur – Levice 2 [DIR] + N-1 Veľký Ďur – Levice 1

[SK-HU] Levice – Gönyű [DIR] [SK] + N-1 Veľké Kapušany – Mukachevo (WPS)

These elements were primarily impacted by substantial transit flows originating from the north-western region towards the south, particularly flows from Czechia (CZ) and Poland (PL) directed towards Hungary (HU). This directional pattern placed considerable stress on the Slovak transmission infrastructure.

In addition to cross-border transit, the Veľký Ďur – Levice lines experienced further loading due to the generation output from the Mochovce nuclear power plant, located in proximity to these elements. This domestic injection contributed significantly to the overall loading on these lines, compounding the need for IVA applications.

Another contributing factor to IVA application on the Veľký Ďur – Levice corridor was the relatively high AMR values, representing the virtual capacity share assigned to these elements. On average, AMR values reached 151 MW in timestamps where reductions were applied, with peak values recorded as high as 421 MW.

Planned outages also played a significant role in increasing system constraints and, consequently, the application of IVA. The most impactful outages during Q3 2025 included:

Veľký Ďur – Gönyű: 25 August – 5 September 2025

Veľké Kapušany – Mukachevo: 1 September – 30 October 2025

Veľký Ďur – Levice 1: 22 September – 25 September 2025

These outages reduced the operational flexibility of the network, especially during periods of already constrained capacity, exacerbating the frequency and scope of IVA application.

Looking ahead, we anticipate that the volume of IVA applications will significantly decrease in the fourth quarter (Q4) of 2025. This expectation is based on the seasonal increase in thermal limits for the winter period, which generally allows for higher permissible loadings on transmission elements, thereby reducing the need for capacity reductions.

Total IVA reductions for Q3/2025

Future developments aimed at reducing the volume of reductions:

Short-term plans:

We aim to improve the quality of the scenario selection in our validation tool in order to validate the forecasted scenario that is closer to the market outcome and has already implemented the minimum floor for the level of the cross-zonal capacities that equals to 20% of minRAM.

Mid-term plans:
  SEPS is currently developing an internal project aimed at exploring the feasibility of implementing Dynamic Line Rating (DLR) on the aforementioned overhead lines. The use of DLR is expected to help alleviate congestion by allowing for more accurate and real-time assessment of line capacity. The initial feasibility study is scheduled to be completed within the current year.

Long-term plans:

There are plans to reconfigure the critical elements at the V. Ďur substation, which are expected to significantly reduce flows on the CNEC NEC [SK-SK] V. Ďur - Levice 2 [DIR] + N-1 V. Ďur - Levice. The current estimate is that this will be accomplished in Q4 2028.

In addition, a reinforcement of the Nosovice–Varín tie-line is planned, which will increase the Imax from 1740 A to 2000 A in 2027. This upgrade is expected to lead to a reduction in the volume of IVA applied to this element.

# Transelectrica

In 2021, the Romanian Government decided to adopt an Action Plan pursuant to Article 15 of the Regulation (EU) 2019/943, including a linear trajectory for the yearly increase of the minimum capacity made available for cross-zonal trade until 31 December 2025.

For year 2025 the minimum capacity made available for cross-zonal trade on Romania – Hungary border (part of Core CCR) has been 63% from the transmission capacity) according to the Action Plan. For this year though, Transelectrica was granted a derogation on foreseeable grounds for maintaining operational security, thus the minimum capacity for cross-border trade has been increased from 33% (compared to the previous year) at 41% from the transmission capacity, the same target provided in the Action Plan for the year of 2022.

In addition to being part of the Core CCR, Transelectrica is also part of SEE CCR with RO – BG border having operational processes for Day-ahead capacity calculation since June 2021 and first Intraday capacity calculation since October 2021. Moreover, there are three non-EU borders for which there is no coordinated capacity calculation.

Regarding the capacity calculation process, the Core DA CCM allows TSOs to correct cross-zonal capacity for reasons of operational security during the validation process individually and in a coordinated way according to Article 20 (1). Article 20(5) states that “each Core TSO shall validate and have the right to decrease the RAM for reasons of operational security during the individual validation. The adjustment due to individual validation is called ‘individual validation adjustment’ (IVA) and it shall have a positive value, i.e. it may only reduce the RAM. IVA may reduce the RAM only to the minimum degree that is needed to ensure operational security considering all expected available costly and non-costly RAs”.

For the period 20250701 – 20250930, Transelectrica applied an Individual Validation Adjustment (IVA) on the CNEs mentioned in Figure 1. In this graph the average IVA per CNE is represented for the timestamps where reductions were applied for more than 1% of the total reductions.

Moreover, the percentage of total applications shows that reductions were applied for the same CNEs, located mainly in the western part of the grid.

Figure 1. Average IVA applied and percentage of total IVA applications per CNE during the reported period

General measures to avoid cross-zonal capacity reductions in the future, as per Art. 20(14)(b) of DA CCM;

Detailed report and action plan describing how such deviations are expected to be alleviated and solved in the future.

Development of the transmission grid

Most of the cases with IVA applications are related to 220 kV critical network elements located in the southwest part of the country. The following measures are foreseen according to the National Action plan in order to increase the remaining available margin of these elements:

New 400 kV OHL Porțile de Fier – Reșița was commissioned in mid November 2024. This new OHL leads to decreasing the loading on the double circuit OHL 220 kV Porțile de Fier – Reșița and thus leading to a lower need of reductions in the future on these two CNEs.

New 400 kV OHL Reșița – Pancevo circuit 2 was commissioned in mid November 2024. 400 kV OHL Reșița – Pancevo circuit 1 will be commissioned in the beginning of 2025. This investment project leads to increasing transfer capacity and improving the system security in the region. Moreover the loading of the critical network element 400 kV OHL Porțile de Fier – Djerdap is expected to decrease enough so that it is not treated as structural congestion anymore;

OHL 400 kV Reșița – Timișoara – Săcălaz d.c. planned for 2026;

OHL 400 kV Timișoara – Arad d.c. planned for 2027;

Increase the transmission capacity for the OHL in the 220 kV axis Urechești – Târgu Jiu Nord – Paroșeni – Baru Mare – Hășdat planned for 2028;

New 400 kV Tieline Suceava – Bălți (RO-MD) planned for 2030;

New 400/220 kV Autotransformer in Roșiori substation planned for 2027.

Increase the quality of the D2CF CGMs at CCR level

At this moment there is no common D2CF CGMs process to be used for DA CC in all CCRs. Each CCR has its own rules on the IGMs (e.g. D2CF for Core TSOs and DACF for the rest of Continental Europe) and a net position forecast to be used when CGMs are created. As there is no common, harmonized and reliable net position or exchange forecast yet implemented in Europe, the assumptions taken by each CCR will lead to large uncertainties, potentially high overloads and operational situations where the available remedial action potential (including redispatching) is insufficient, thus leading to applying reductions on CNECs. This situation affects the power flow on the 220 kV critical network elements located especially in the southwest part of the country, heavily influenced by the exchanges in the SEE region where DACF files are used for the purpose of D2CF CGMs in Core CCR. A common D2CF CGM process is required for all CCRs in Continental Europe as soon as possible.

Implementation of the coordinated validation in the Core CCR

Coordinated validation would allow TSOs to use commonly the remedial actions available throughout Core CCR, making use of the most suitable remedial action in order to secure a minimum capacity and reduce the IVA applications.

Implementation of regional coordinated processes for security analysis

The Articles 16(4) and 16(8) of the Regulation (EU) 2019/943 refers to the implementation of the coordinated capacity calculation and security analysis at regional level to ensure a minimum capacity available for cross-zonal trade. Though the capacity calculation using flow-based method in Core CCR is now an operational process, it is not enough to comply with the minimum available capacity requirements. The results of the day-ahead capacity calculation come with a lot of uncertainties without a coordinated security analysis implemented at a regional level before real-time. Not always the internal measures and remedial actions estimated as available for day-ahead capacity calculation are available and enough to maintain the system security in real-time.

Implementation of redispatching and countertrading processes implemented at regional level pursuant to Article 35 and 74 of Regulation (EU) 2015/1222.

The Article 16(4) of the Regulation (EU) 2019/943 stated that the redispatching and countertrading shall be used to maximize the available capacity to reach the minimum capacity provided for in Article 16(8) of the Regulation (EU) 2019/943. This process shall be coordinated and follow the implementation of cost-sharing methodology. At Core CCR level these processes are under implementation. Because of this Transelectrica applies an individual redispatching process aimed at achieving the minimum level of cross-zonal capacity as per national Action Plan. This is not always feasible due to the lack of sufficient remedial actions.

Coordination between capacity calculation regions

Besides Core CCR, CNTEE Transelectrica SA is also part of two other CCRs, with Romania – Bulgaria border in SEE CCR, Romania – Hungary border in Core CCR and Romania – Ukraine, Romania – Republic of Moldova borders in Eastern Europe (EE) CCR. For Romania – Serbia there is no coordinated capacity calculation at the present moment. The exchanges on the borders with Bulgaria, Serbia, Ukraine and Republic of Moldova are considered as fixed in coordinated capacity calculation from Core CCR. Any deviation from these values forecasted two days ahead will create a different loading on the critical network element with risks for the operational security of the system. Because of this, lack of cross-CCR coordination becomes critical for Romania in cases with high export from the southeast part of Continental Europe towards the central area. These uncoordinated transits through Romania correlated with high generation in the wind and hydro power plants from the south part of Romania lead to increasing the power flows on the 220 kV network in the southwest part of the country. These transits create (N-1) violations in the transmission grid which cannot be addressed without coordinated remedial actions for redispatching and countertrading.

REPORT OF THE GERMAN TRANSMISSION SYSTEM OPERATORS ON AVAILABLE CROSS-ZONAL CAPACITY FOR THE YEAR 2023 PURSUANT TO ARTICLE 15(4) INTERNAL MARKET FOR ELECTRICITY REGULATION (EU) 2019/943;  URL: https://www.netztransparenz.de/en/Electricity-market-design/Clean-Energy-Package

Federal Ministry for Economic Affairs and Climate Action (2020): Action Plan Bidding Zone; URL: https://www.bmwk.de/Redaktion/EN/Downloads/a/action-plan-bidding-zone.html

50Hertz Transmission GmbH, Amprion GmbH, Tennet TSO GmbH, TransnetBW GmbH  (2023): Grid Development Plan Electricity 2037/2045 – 2nd Draft; URL: https://www.netzentwicklungsplan.de/en/front